## Chiller
Chiller Name | Reference Capacity | Reference COP | Reference Leaving Chilled Water Temperature | Reference Entering Condenser Fluid Temperature | Reference Evaporator Volumetric Water Flow Rate | Reference Condenser Volumetric Water Flow Rate | Cooling Capacity Function of Temperature Curve | Electric Input to Cooling Output Ratio Function of Temperature Curve | Electric Input to Cooling Output Ratio Function of Part Load Ratio Curve | Minimum Part Load Ratio | Maximum Part Load Ratio | Optimum Part Load Ratio | Minimum Unloading Ratio | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | Condenser Type | Condenser Fan Power Ratio | Compressor Motor Efficiency | Leaving Chilled Water Lower Temperature Limit | Chiller Evaporator Flow Mode | Reference Heat Recovery Water Flow Rate | Heat Recovery Inlet Node | Heat Recovery Outlet Node
制冷机名称 | 参考制冷量 | 参考COP | 制冷机出水参考温度 | 冷凝器入水参考温度 | 蒸发器参考水流量 | 冷凝器参考水流量 | 制冷量与温度的函数曲线 | EIR与温度的函数曲线 | EIR与部分负荷的函数曲线 | 部分负荷率下限 | 部分负荷率上限 | 最优部分负荷率 | 最小卸载率 | 冷冻水测进水点 | 冷冻水测出水点 | 冷凝侧入口点 | 冷凝侧出口点 | 冷凝器类型 | 冷凝器风机功率 | 冷凝器发动机效率 | 冷冻水出口温度下限 | 冷冻水流量控制方式 | 热回收设计水流量 | 热回收入口点 | 热回收出口点
| W | W/W | C | C | m3/s | m3/s | [12 empty] | W/W |  | C |  | m3/s
ElectricEIRChiller McQuay WSC 471kW/5.89COP/Vanes | 471200 | 5.89 | 8.89 | 26.67 | .01035 | .01924 | ElectricEIRChiller McQuay WSC 471kW/5.89COP/Vanes CAPFT | ElectricEIRChiller McQuay WSC 471kW/5.89COP/Vanes EIRFT | ElectricEIRChiller McQuay WSC 471kW/5.89COP/Vanes EIRFPLR | .10 | 1.15 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 563kW/10.61COP/Vanes | 562600 | 10.61 | 6.11 | 12.78 | .01514 | .0241 | ElectricEIRChiller York YT 563kW/10.61COP/Vanes CAPFT | ElectricEIRChiller York YT 563kW/10.61COP/Vanes EIRFT | ElectricEIRChiller York YT 563kW/10.61COP/Vanes EIRFPLR | .09 | 1.03 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PEH 703kW/7.03COP/Vanes | 703300 | 7.03 | 5.56 | 22.78 | .02019 | .02902 | ElectricEIRChiller McQuay PEH 703kW/7.03COP/Vanes CAPFT | ElectricEIRChiller McQuay PEH 703kW/7.03COP/Vanes EIRFT | ElectricEIRChiller McQuay PEH 703kW/7.03COP/Vanes EIRFPLR | .10 | 1.03 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 23XL 724kW/6.04COP/Vanes | 724400 | 6.04 | 5.56 | 21.11 | .01779 | .01956 | ElectricEIRChiller Carrier 23XL 724kW/6.04COP/Vanes CAPFT | ElectricEIRChiller Carrier 23XL 724kW/6.04COP/Vanes EIRFT | ElectricEIRChiller Carrier 23XL 724kW/6.04COP/Vanes EIRFPLR | .19 | 1.04 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 742kW/5.42COP/VSD | 742000 | 5.42 | 5.56 | 21.11 | .01779 | .01956 | ElectricEIRChiller Carrier 19XR 742kW/5.42COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 742kW/5.42COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 742kW/5.42COP/VSD EIRFPLR | .19 | 1.02 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay WSC 816kW/6.74COP/Vanes | 815800 | 6.74 | 8.89 | 26.67 | .01748 | .04164 | ElectricEIRChiller McQuay WSC 816kW/6.74COP/Vanes CAPFT | ElectricEIRChiller McQuay WSC 816kW/6.74COP/Vanes EIRFT | ElectricEIRChiller McQuay WSC 816kW/6.74COP/Vanes EIRFPLR | .09 | 1.03 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PEH 819kW/8.11COP/Vanes | 819300 | 8.11 | 4.44 | 12.78 | .02524 | .03785 | ElectricEIRChiller McQuay PEH 819kW/8.11COP/Vanes CAPFT | ElectricEIRChiller McQuay PEH 819kW/8.11COP/Vanes EIRFT | ElectricEIRChiller McQuay PEH 819kW/8.11COP/Vanes EIRFPLR | .09 | 1.05 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 823kW/6.28COP/Vanes | 822900 | 6.28 | 5.56 | 23.89 | .03186 | .04744 | ElectricEIRChiller Carrier 19XR 823kW/6.28COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 823kW/6.28COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 823kW/6.28COP/Vanes EIRFPLR | .10 | 1.03 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 869kW/5.57COP/VSD | 868600 | 5.57 | 8.89 | 26.67 | .01754 | .02593 | ElectricEIRChiller Carrier 19XR 869kW/5.57COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 869kW/5.57COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 869kW/5.57COP/VSD EIRFPLR | .18 | 1.03 | 1.0 | .18 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 897kW/7.23COP/VSD | 896700 | 7.23 | 9.82 | 23.89 | .06782 | .0436 | ElectricEIRChiller Carrier 19XR 897kW/7.23COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 897kW/7.23COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 897kW/7.23COP/VSD EIRFPLR | .20 | 1.04 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 897kW/6.50COP/Vanes | 896700 | 6.50 | 9.82 | 23.89 | .06782 | .04423 | ElectricEIRChiller Carrier 19XR 897kW/6.50COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 897kW/6.50COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 897kW/6.50COP/Vanes EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 897kW/7.60COP/VSD | 896700 | 7.60 | 9.83 | 22.78 | .06782 | .05142 | ElectricEIRChiller York YT 897kW/7.60COP/VSD CAPFT | ElectricEIRChiller York YT 897kW/7.60COP/VSD EIRFT | ElectricEIRChiller York YT 897kW/7.60COP/VSD EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 897kW/6.27COP/VSD | 896700 | 6.27 | 6.67 | 22.78 | .06782 | .05142 | ElectricEIRChiller York YT 897kW/6.27COP/VSD CAPFT | ElectricEIRChiller York YT 897kW/6.27COP/VSD EIRFT | ElectricEIRChiller York YT 897kW/6.27COP/VSD EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 897kW/6.23COP/VSD | 896700 | 6.23 | 6.67 | 23.89 | .06782 | .04442 | ElectricEIRChiller Carrier 19XR 897kW/6.23COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 897kW/6.23COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 897kW/6.23COP/VSD EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PFH 932kW/5.09COP/Vanes | 931900 | 5.09 | 4.44 | 26.11 | .03785 | .04732 | ElectricEIRChiller McQuay PFH 932kW/5.09COP/Vanes CAPFT | ElectricEIRChiller McQuay PFH 932kW/5.09COP/Vanes EIRFT | ElectricEIRChiller McQuay PFH 932kW/5.09COP/Vanes EIRFPLR | .09 | 1.02 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 960kW/4.64COP/Vanes | 960000 | 4.64 | 4.44 | 26.11 | .03785 | .04732 | ElectricEIRChiller York YT 960kW/4.64COP/Vanes CAPFT | ElectricEIRChiller York YT 960kW/4.64COP/Vanes EIRFT | ElectricEIRChiller York YT 960kW/4.64COP/Vanes EIRFPLR | .09 | 1.09 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1023kW/5.81COP/Vanes | 1023300 | 5.81 | 6.67 | 29.44 | .02366 | .04732 | ElectricEIRChiller York YT 1023kW/5.81COP/Vanes CAPFT | ElectricEIRChiller York YT 1023kW/5.81COP/Vanes EIRFT | ElectricEIRChiller York YT 1023kW/5.81COP/Vanes EIRFPLR | .09 | 1.06 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PEH 1030kW/8.58COP/Vanes | 1030300 | 8.58 | 6.11 | 12.78 | .02378 | .03407 | ElectricEIRChiller McQuay PEH 1030kW/8.58COP/Vanes CAPFT | ElectricEIRChiller McQuay PEH 1030kW/8.58COP/Vanes EIRFT | ElectricEIRChiller McQuay PEH 1030kW/8.58COP/Vanes EIRFPLR | .08 | 1.02 | 1.0 | .08 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1048kW/6.06COP/Vanes | 1047900 | 6.06 | 6.67 | 29.44 | .04542 | .05678 | ElectricEIRChiller York YT 1048kW/6.06COP/Vanes CAPFT | ElectricEIRChiller York YT 1048kW/6.06COP/Vanes EIRFT | ElectricEIRChiller York YT 1048kW/6.06COP/Vanes EIRFPLR | .10 | 1.06 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1055kW/5.96COP/Vanes | 1055000 | 5.96 | 6.67 | 29.44 | .02839 | .05678 | ElectricEIRChiller York YT 1055kW/5.96COP/Vanes CAPFT | ElectricEIRChiller York YT 1055kW/5.96COP/Vanes EIRFT | ElectricEIRChiller York YT 1055kW/5.96COP/Vanes EIRFPLR | .10 | 1.05 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1076kW/5.52COP/Vanes | 1076100 | 5.52 | 5.56 | 24.89 | .03186 | .04744 | ElectricEIRChiller Carrier 19XR 1076kW/5.52COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1076kW/5.52COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1076kW/5.52COP/Vanes EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHE 1080kW/7.39COP/Vanes | 1079600 | 7.39 | 5.56 | 23.61 | .03186 | .06416 | ElectricEIRChiller Trane CVHE 1080kW/7.39COP/Vanes CAPFT | ElectricEIRChiller Trane CVHE 1080kW/7.39COP/Vanes EIRFT | ElectricEIRChiller Trane CVHE 1080kW/7.39COP/Vanes EIRFPLR | .20 | 1.05 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1090kW/7.57COP/VSD | 1090100 | 7.57 | 6.67 | 22.78 | .06782 | .05142 | ElectricEIRChiller York YT 1090kW/7.57COP/VSD CAPFT | ElectricEIRChiller York YT 1090kW/7.57COP/VSD EIRFT | ElectricEIRChiller York YT 1090kW/7.57COP/VSD EIRFPLR | .14 | 1.02 | 1.0 | .14 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PEH 1104kW/8.00COP/Vanes | 1104200 | 8.00 | 6.67 | 12.78 | .02423 | .03028 | ElectricEIRChiller McQuay PEH 1104kW/8.00COP/Vanes CAPFT | ElectricEIRChiller McQuay PEH 1104kW/8.00COP/Vanes EIRFT | ElectricEIRChiller McQuay PEH 1104kW/8.00COP/Vanes EIRFPLR | .08 | 1.03 | 1.0 | .08 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1125kW/7.92COP/VSD | 1125300 | 7.92 | 6.11 | 12.78 | .03243 | .05173 | ElectricEIRChiller York YT 1125kW/7.92COP/VSD CAPFT | ElectricEIRChiller York YT 1125kW/7.92COP/VSD EIRFT | ElectricEIRChiller York YT 1125kW/7.92COP/VSD EIRFPLR | .09 | 1.03 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHE 1125kW/4.89COP/Vanes | 1125300 | 4.89 | 5.56 | 23.89 | .02776 | .02618 | ElectricEIRChiller Trane CVHE 1125kW/4.89COP/Vanes CAPFT | ElectricEIRChiller Trane CVHE 1125kW/4.89COP/Vanes EIRFT | ElectricEIRChiller Trane CVHE 1125kW/4.89COP/Vanes EIRFPLR | .10 | 1.01 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1125kW/7.92COP/VSD | 1125300 | 7.92 | 6.11 | 12.78 | .03243 | .05173 | ElectricEIRChiller York YT 1125kW/7.92COP/VSD CAPFT | ElectricEIRChiller York YT 1125kW/7.92COP/VSD EIRFT | ElectricEIRChiller York YT 1125kW/7.92COP/VSD EIRFPLR | .09 | 1.03 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHE 1129kW/7.19COP/Vanes | 1128800 | 7.19 | 5.56 | 23.89 | .02776 | .05142 | ElectricEIRChiller Trane CVHE 1129kW/7.19COP/Vanes CAPFT | ElectricEIRChiller Trane CVHE 1129kW/7.19COP/Vanes EIRFT | ElectricEIRChiller Trane CVHE 1129kW/7.19COP/Vanes EIRFPLR | .15 | 1.06 | 1.0 | .15 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1143kW/6.57COP/VSD | 1142900 | 6.57 | 10.00 | 26.67 | .02593 | .05142 | ElectricEIRChiller Carrier 19XR 1143kW/6.57COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1143kW/6.57COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1143kW/6.57COP/VSD EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1157kW/5.62COP/VSD | 1156900 | 5.62 | 5.56 | 21.11 | .02801 | .03186 | ElectricEIRChiller Carrier 19XR 1157kW/5.62COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1157kW/5.62COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1157kW/5.62COP/VSD EIRFPLR | .19 | 1.01 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1196kW/6.50COP/Vanes | 1195600 | 6.50 | 7.22 | 23.89 | .03426 | .04252 | ElectricEIRChiller Carrier 19XR 1196kW/6.50COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1196kW/6.50COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1196kW/6.50COP/Vanes EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1213kW/7.78COP/Vanes | 1213200 | 7.78 | 6.11 | 12.78 | .03243 | .04782 | ElectricEIRChiller Carrier 19XR 1213kW/7.78COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1213kW/7.78COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1213kW/7.78COP/Vanes EIRFPLR | .17 | 1.02 | 1.0 | .17 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PEH 1231kW/6.18COP/Vanes | 1230800 | 6.18 | 5.56 | 22.78 | .03533 | .0511 | ElectricEIRChiller McQuay PEH 1231kW/6.18COP/Vanes CAPFT | ElectricEIRChiller McQuay PEH 1231kW/6.18COP/Vanes EIRFT | ElectricEIRChiller McQuay PEH 1231kW/6.18COP/Vanes EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1234kW/5.39COP/VSD | 1234300 | 5.39 | 8.89 | 26.67 | .02593 | .03861 | ElectricEIRChiller Carrier 19XR 1234kW/5.39COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1234kW/5.39COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1234kW/5.39COP/VSD EIRFPLR | .19 | 1.02 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1259kW/6.26COP/Vanes | 1258900 | 6.26 | 8.89 | 26.67 | .02593 | .03823 | ElectricEIRChiller Carrier 19XR 1259kW/6.26COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1259kW/6.26COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1259kW/6.26COP/Vanes EIRFPLR | .18 | 1.03 | 1.0 | .18 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 1259kW/6.45COP/Vanes | 1258900 | 6.45 | 8.89 | 26.67 | .02631 | .06246 | ElectricEIRChiller York YK 1259kW/6.45COP/Vanes CAPFT | ElectricEIRChiller York YK 1259kW/6.45COP/Vanes EIRFT | ElectricEIRChiller York YK 1259kW/6.45COP/Vanes EIRFPLR | .18 | 1.02 | 1.0 | .18 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1266kW/4.39COP/Vanes | 1266000 | 4.39 | 5.56 | 35.00 | .03533 | .05773 | ElectricEIRChiller York YT 1266kW/4.39COP/Vanes CAPFT | ElectricEIRChiller York YT 1266kW/4.39COP/Vanes EIRFT | ElectricEIRChiller York YT 1266kW/4.39COP/Vanes EIRFPLR | .11 | 1.05 | 1.0 | .11 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes | 1283500 | 6.20 | 5.56 | 22.78 | .03684 | .05337 | ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes | 1283500 | 6.20 | 5.56 | 22.78 | .03684 | .05337 | ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1294kW/7.61COP/Vanes | 1294100 | 7.61 | 6.11 | 12.78 | .03243 | .04732 | ElectricEIRChiller Carrier 19XR 1294kW/7.61COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1294kW/7.61COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1294kW/7.61COP/Vanes EIRFPLR | .16 | 1.02 | 1.0 | .16 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHE 1329kW/5.38COP/Vanes | 1329300 | 5.38 | 6.11 | 29.44 | .04732 | .07098 | ElectricEIRChiller Trane CVHE 1329kW/5.38COP/Vanes CAPFT | ElectricEIRChiller Trane CVHE 1329kW/5.38COP/Vanes EIRFT | ElectricEIRChiller Trane CVHE 1329kW/5.38COP/Vanes EIRFPLR | .29 | 1.05 | 1.0 | .29 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1350kW/7.90COP/VSD | 1350400 | 7.90 | 5.56 | 12.78 | .03684 | .05337 | ElectricEIRChiller Carrier 19XR 1350kW/7.90COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1350kW/7.90COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1350kW/7.90COP/VSD EIRFPLR | .19 | 1.02 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1368kW/7.35COP/VSD | 1367900 | 7.35 | 5.56 | 23.89 | .05047 | .07571 | ElectricEIRChiller York YT 1368kW/7.35COP/VSD CAPFT | ElectricEIRChiller York YT 1368kW/7.35COP/VSD EIRFT | ElectricEIRChiller York YT 1368kW/7.35COP/VSD EIRFPLR | .10 | 1.03 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHE 1372kW/7.49COP/Vanes | 1371500 | 7.49 | 5.56 | 23.89 | .05047 | .07571 | ElectricEIRChiller Trane CVHE 1372kW/7.49COP/Vanes CAPFT | ElectricEIRChiller Trane CVHE 1372kW/7.49COP/Vanes EIRFT | ElectricEIRChiller Trane CVHE 1372kW/7.49COP/Vanes EIRFPLR | .41 | 1.07 | 1.0 | .41 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1396kW/7.35COP/Vanes | 1396100 | 7.35 | 5.56 | 23.89 | .05047 | .07571 | ElectricEIRChiller York YT 1396kW/7.35COP/Vanes CAPFT | ElectricEIRChiller York YT 1396kW/7.35COP/Vanes EIRFT | ElectricEIRChiller York YT 1396kW/7.35COP/Vanes EIRFPLR | .10 | 1.03 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1403kW/7.09COP/VSD | 1403100 | 7.09 | 6.67 | 12.78 | .03426 | .04252 | ElectricEIRChiller Carrier 19XR 1403kW/7.09COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1403kW/7.09COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1403kW/7.09COP/VSD EIRFPLR | .17 | 1.03 | 1.0 | .17 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1403kW/6.94COP/VSD | 1403100 | 6.94 | 5.56 | 23.89 | .05047 | .05047 | ElectricEIRChiller York YT 1403kW/6.94COP/VSD CAPFT | ElectricEIRChiller York YT 1403kW/6.94COP/VSD EIRFT | ElectricEIRChiller York YT 1403kW/6.94COP/VSD EIRFPLR | .10 | 1.1 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHE 1407kW/7.14COP/VSD | 1406600 | 7.14 | 5.56 | 23.89 | .05047 | .07571 | ElectricEIRChiller Trane CVHE 1407kW/7.14COP/VSD CAPFT | ElectricEIRChiller Trane CVHE 1407kW/7.14COP/VSD EIRFT | ElectricEIRChiller Trane CVHE 1407kW/7.14COP/VSD EIRFPLR | .30 | 1.06 | 1.0 | .30 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PFH 1407kW/6.60COP/Vanes | 1406600 | 6.60 | 5.56 | 22.78 | .04038 | .05804 | ElectricEIRChiller McQuay PFH 1407kW/6.60COP/Vanes CAPFT | ElectricEIRChiller McQuay PFH 1407kW/6.60COP/Vanes EIRFT | ElectricEIRChiller McQuay PFH 1407kW/6.60COP/Vanes EIRFPLR | .10 | 1.04 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1407kW/6.04COP/VSD | 1406600 | 6.04 | 6.67 | 29.44 | .06057 | .07571 | ElectricEIRChiller Carrier 19XR 1407kW/6.04COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1407kW/6.04COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1407kW/6.04COP/VSD EIRFPLR | .20 | 1.04 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1410kW/8.54COP/VSD | 1410100 | 8.54 | 6.11 | 12.78 | .04 | .05861 | ElectricEIRChiller Carrier 19XR 1410kW/8.54COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1410kW/8.54COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1410kW/8.54COP/VSD EIRFPLR | .18 | 1.03 | 1.0 | .18 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHE 1442kW/6.61COP/VSD | 1441800 | 6.61 | 5.56 | 23.89 | .05047 | .05047 | ElectricEIRChiller Trane CVHE 1442kW/6.61COP/VSD CAPFT | ElectricEIRChiller Trane CVHE 1442kW/6.61COP/VSD EIRFT | ElectricEIRChiller Trane CVHE 1442kW/6.61COP/VSD EIRFPLR | .10 | 1.07 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1459kW/6.40COP/VSD | 1459400 | 6.40 | 5.56 | 23.89 | .05047 | .05047 | ElectricEIRChiller York YT 1459kW/6.40COP/VSD CAPFT | ElectricEIRChiller York YT 1459kW/6.40COP/VSD EIRFT | ElectricEIRChiller York YT 1459kW/6.40COP/VSD EIRFPLR | .10 | 1.13 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHE 1484kW/9.96COP/VSD | 1484000 | 9.96 | 4.44 | 12.78 | .07571 | .09085 | ElectricEIRChiller Trane CVHE 1484kW/9.96COP/VSD CAPFT | ElectricEIRChiller Trane CVHE 1484kW/9.96COP/VSD EIRFT | ElectricEIRChiller Trane CVHE 1484kW/9.96COP/VSD EIRFPLR | .24 | 1.06 | 1.0 | .24 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1495kW/7.51COP/VSD | 1494500 | 7.51 | 7.22 | 23.89 | .0429 | .06719 | ElectricEIRChiller York YT 1495kW/7.51COP/VSD CAPFT | ElectricEIRChiller York YT 1495kW/7.51COP/VSD EIRFT | ElectricEIRChiller York YT 1495kW/7.51COP/VSD EIRFPLR | .11 | 1.05 | 1.0 | .11 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay WSC 1519kW/7.10COP/Vanes | 1519200 | 7.10 | 8.89 | 26.67 | .03186 | .08139 | ElectricEIRChiller McQuay WSC 1519kW/7.10COP/Vanes CAPFT | ElectricEIRChiller McQuay WSC 1519kW/7.10COP/Vanes EIRFT | ElectricEIRChiller McQuay WSC 1519kW/7.10COP/Vanes EIRFPLR | .10 | 1.03 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1558kW/5.81COP/VSD | 1557800 | 5.81 | 5.56 | 21.11 | .03785 | .05142 | ElectricEIRChiller Carrier 19XR 1558kW/5.81COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1558kW/5.81COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1558kW/5.81COP/VSD EIRFPLR | .19 | 1.01 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1586kW/5.53COP/VSD | 1586000 | 5.53 | 8.89 | 26.67 | .03388 | .04669 | ElectricEIRChiller Carrier 19XR 1586kW/5.53COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1586kW/5.53COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1586kW/5.53COP/VSD EIRFPLR | .19 | 1.01 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PEH 1635kW/7.47COP/Vanes | 1635200 | 7.47 | 4.44 | 12.78 | .04416 | .06624 | ElectricEIRChiller McQuay PEH 1635kW/7.47COP/Vanes CAPFT | ElectricEIRChiller McQuay PEH 1635kW/7.47COP/Vanes EIRFT | ElectricEIRChiller McQuay PEH 1635kW/7.47COP/Vanes EIRFPLR | .08 | 1.03 | 1.0 | .08 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1635kW/6.36COP/Vanes | 1635200 | 6.36 | 8.89 | 26.67 | .03432 | .05035 | ElectricEIRChiller Carrier 19XR 1635kW/6.36COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1635kW/6.36COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1635kW/6.36COP/Vanes EIRFPLR | .18 | 1.05 | 1.0 | .18 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1656kW/8.24COP/VSD | 1656300 | 8.24 | 6.11 | 12.78 | .04322 | .06296 | ElectricEIRChiller Carrier 19XR 1656kW/8.24COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1656kW/8.24COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1656kW/8.24COP/VSD EIRFPLR | .17 | 1.04 | 1.0 | .17 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1663kW/9.34COP/Vanes | 1663300 | 9.34 | 5.56 | 12.78 | .04139 | .0776 | ElectricEIRChiller York YT 1663kW/9.34COP/Vanes CAPFT | ElectricEIRChiller York YT 1663kW/9.34COP/Vanes EIRFT | ElectricEIRChiller York YT 1663kW/9.34COP/Vanes EIRFPLR | .17 | 1.03 | 1.0 | .17 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XL 1674kW/7.89COP/Vanes | 1673900 | 7.89 | 4.44 | 12.78 | .07571 | .09085 | ElectricEIRChiller Carrier 19XL 1674kW/7.89COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XL 1674kW/7.89COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XL 1674kW/7.89COP/Vanes EIRFPLR | .32 | 1.02 | 1.0 | .32 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 1681kW/6.59COP/Vanes | 1680900 | 6.59 | 5.56 | 23.89 | .04366 | .05142 | ElectricEIRChiller Trane CVHF 1681kW/6.59COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 1681kW/6.59COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 1681kW/6.59COP/Vanes EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1723kW/8.32COP/VSD | 1723100 | 8.32 | 6.11 | 12.78 | .04757 | .06934 | ElectricEIRChiller Carrier 19XR 1723kW/8.32COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1723kW/8.32COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1723kW/8.32COP/VSD EIRFPLR | .18 | 1.04 | 1.0 | .18 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1727kW/9.04COP/Vanes | 1726600 | 9.04 | 7.78 | 12.78 | .03912 | .07192 | ElectricEIRChiller Carrier 19XR 1727kW/9.04COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1727kW/9.04COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1727kW/9.04COP/Vanes EIRFPLR | .17 | 1.03 | 1.0 | .17 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay WSC 1751kW/6.73COP/Vanes | 1751300 | 6.73 | 8.89 | 26.67 | .04145 | .09337 | ElectricEIRChiller McQuay WSC 1751kW/6.73COP/Vanes CAPFT | ElectricEIRChiller McQuay WSC 1751kW/6.73COP/Vanes EIRFT | ElectricEIRChiller McQuay WSC 1751kW/6.73COP/Vanes EIRFPLR | .10 | 1.06 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 1758kW/5.96COP/Vanes | 1758300 | 5.96 | 5.56 | 24.44 | .06309 | .06309 | ElectricEIRChiller Trane CVHF 1758kW/5.96COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 1758kW/5.96COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 1758kW/5.96COP/Vanes EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1758kW/5.76COP/VSD | 1758300 | 5.76 | 5.56 | 24.44 | .06309 | .06309 | ElectricEIRChiller York YT 1758kW/5.76COP/VSD CAPFT | ElectricEIRChiller York YT 1758kW/5.76COP/VSD EIRFT | ElectricEIRChiller York YT 1758kW/5.76COP/VSD EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1758kW/6.26COP/Vanes | 1758300 | 6.26 | 5.56 | 24.44 | .06309 | .06309 | ElectricEIRChiller York YT 1758kW/6.26COP/Vanes CAPFT | ElectricEIRChiller York YT 1758kW/6.26COP/Vanes EIRFT | ElectricEIRChiller York YT 1758kW/6.26COP/Vanes EIRFPLR | .10 | 1.14 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1758kW/5.96COP/Vanes | 1758300 | 5.96 | 5.56 | 24.44 | .06309 | .06309 | ElectricEIRChiller York YT 1758kW/5.96COP/Vanes CAPFT | ElectricEIRChiller York YT 1758kW/5.96COP/Vanes EIRFT | ElectricEIRChiller York YT 1758kW/5.96COP/Vanes EIRFPLR | .10 | 1.01 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHE 1758kW/5.96COP/Vanes | 1758300 | 5.96 | 6.67 | 29.44 | .07571 | .09464 | ElectricEIRChiller Trane CVHE 1758kW/5.96COP/Vanes CAPFT | ElectricEIRChiller Trane CVHE 1758kW/5.96COP/Vanes EIRFT | ElectricEIRChiller Trane CVHE 1758kW/5.96COP/Vanes EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1758kW/6.28COP/Vanes | 1758300 | 6.28 | 6.67 | 29.44 | .07571 | .09464 | ElectricEIRChiller York YT 1758kW/6.28COP/Vanes CAPFT | ElectricEIRChiller York YT 1758kW/6.28COP/Vanes EIRFT | ElectricEIRChiller York YT 1758kW/6.28COP/Vanes EIRFPLR | .20 | 1.06 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1758kW/5.86COP/VSD | 1758300 | 5.86 | 5.56 | 24.44 | .06303 | .07337 | ElectricEIRChiller Carrier 19XR 1758kW/5.86COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1758kW/5.86COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1758kW/5.86COP/VSD EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 1758kW/6.46COP/VSD | 1758300 | 6.46 | 5.56 | 24.44 | .06309 | .06309 | ElectricEIRChiller Trane CVHF 1758kW/6.46COP/VSD CAPFT | ElectricEIRChiller Trane CVHF 1758kW/6.46COP/VSD EIRFT | ElectricEIRChiller Trane CVHF 1758kW/6.46COP/VSD EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 1758kW/6.87COP/Vanes | 1758300 | 6.87 | 5.56 | 24.44 | .06309 | .06309 | ElectricEIRChiller Trane CVHF 1758kW/6.87COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 1758kW/6.87COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 1758kW/6.87COP/Vanes EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1776kW/8.00COP/Vanes | 1775900 | 8.00 | 6.11 | 12.78 | .04757 | .07003 | ElectricEIRChiller Carrier 19XR 1776kW/8.00COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 1776kW/8.00COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 1776kW/8.00COP/Vanes EIRFPLR | .17 | 1.04 | 1.0 | .17 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XL 1779kW/6.18COP/Vanes | 1779400 | 6.18 | 6.67 | 26.11 | .06303 | .08858 | ElectricEIRChiller Carrier 19XL 1779kW/6.18COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XL 1779kW/6.18COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XL 1779kW/6.18COP/Vanes EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 1779kW/6.18COP/Vanes | 1779400 | 6.18 | 5.56 | 23.89 | .04454 | .05142 | ElectricEIRChiller Trane CVHF 1779kW/6.18COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 1779kW/6.18COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 1779kW/6.18COP/Vanes EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1794kW/8.11COP/Vanes | 1793500 | 8.11 | 7.22 | 23.89 | .05148 | .09653 | ElectricEIRChiller York YT 1794kW/8.11COP/Vanes CAPFT | ElectricEIRChiller York YT 1794kW/8.11COP/Vanes EIRFT | ElectricEIRChiller York YT 1794kW/8.11COP/Vanes EIRFPLR | .10 | 1.08 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1794kW/7.90COP/VSD | 1793500 | 7.90 | 7.22 | 23.89 | .05148 | .09653 | ElectricEIRChiller York YT 1794kW/7.90COP/VSD CAPFT | ElectricEIRChiller York YT 1794kW/7.90COP/VSD EIRFT | ElectricEIRChiller York YT 1794kW/7.90COP/VSD EIRFPLR | .10 | 1.05 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XL 1797kW/5.69COP/Vanes | 1797000 | 5.69 | 6.67 | 29.44 | .07737 | .09672 | ElectricEIRChiller Carrier 19XL 1797kW/5.69COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XL 1797kW/5.69COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XL 1797kW/5.69COP/Vanes EIRFPLR | .39 | 1.01 | 1.0 | .39 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 1801kW/6.34COP/VSD | 1800500 | 6.34 | 7.22 | 23.89 | .05161 | .06385 | ElectricEIRChiller Carrier 19XR 1801kW/6.34COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 1801kW/6.34COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 1801kW/6.34COP/VSD EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1867kW/10.09COP/Vanes | 1867300 | 10.09 | 7.78 | 12.78 | .07571 | .09085 | ElectricEIRChiller York YT 1867kW/10.09COP/Vanes CAPFT | ElectricEIRChiller York YT 1867kW/10.09COP/Vanes EIRFT | ElectricEIRChiller York YT 1867kW/10.09COP/Vanes EIRFPLR | .09 | 1.04 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XL 1871kW/6.49COP/Vanes | 1870800 | 6.49 | 6.67 | 26.11 | .06303 | .0877 | ElectricEIRChiller Carrier 19XL 1871kW/6.49COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XL 1871kW/6.49COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XL 1871kW/6.49COP/Vanes EIRFPLR | .19 | 1.02 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1881kW/6.77COP/VSD | 1881400 | 6.77 | 6.67 | 23.89 | .07571 | .09464 | ElectricEIRChiller York YT 1881kW/6.77COP/VSD CAPFT | ElectricEIRChiller York YT 1881kW/6.77COP/VSD EIRFT | ElectricEIRChiller York YT 1881kW/6.77COP/VSD EIRFPLR | .09 | 1.03 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 1881kW/6.53COP/Vanes | 1881400 | 6.53 | 8.89 | 26.67 | .04397 | .1041 | ElectricEIRChiller York YK 1881kW/6.53COP/Vanes CAPFT | ElectricEIRChiller York YK 1881kW/6.53COP/Vanes EIRFT | ElectricEIRChiller York YK 1881kW/6.53COP/Vanes EIRFPLR | .19 | 1.03 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 1881kW/6.53COP/Vanes | 1881400 | 6.53 | 8.89 | 26.67 | .04397 | .1041 | ElectricEIRChiller York YK 1881kW/6.53COP/Vanes CAPFT | ElectricEIRChiller York YK 1881kW/6.53COP/Vanes EIRFT | ElectricEIRChiller York YK 1881kW/6.53COP/Vanes EIRFPLR | .19 | 1.03 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PEH 1895kW/6.42COP/Vanes | 1895400 | 6.42 | 6.67 | 23.89 | .07571 | .09085 | ElectricEIRChiller McQuay PEH 1895kW/6.42COP/Vanes CAPFT | ElectricEIRChiller McQuay PEH 1895kW/6.42COP/Vanes EIRFT | ElectricEIRChiller McQuay PEH 1895kW/6.42COP/Vanes EIRFPLR | .09 | 1.09 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 1934kW/7.55COP/Vanes | 1934100 | 7.55 | 5.56 | 13.89 | .05552 | .08675 | ElectricEIRChiller York YT 1934kW/7.55COP/Vanes CAPFT | ElectricEIRChiller York YT 1934kW/7.55COP/Vanes EIRFT | ElectricEIRChiller York YT 1934kW/7.55COP/Vanes EIRFPLR | .10 | 1.06 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PEH 1934kW/6.01COP/Vanes | 1934100 | 6.01 | 5.56 | 22.78 | .05552 | .07981 | ElectricEIRChiller McQuay PEH 1934kW/6.01COP/Vanes CAPFT | ElectricEIRChiller McQuay PEH 1934kW/6.01COP/Vanes EIRFT | ElectricEIRChiller McQuay PEH 1934kW/6.01COP/Vanes EIRFPLR | .10 | 1.08 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay WDC 1973kW/6.28COP/Vanes | 1972800 | 6.28 | 8.89 | 26.67 | .04145 | .09337 | ElectricEIRChiller McQuay WDC 1973kW/6.28COP/Vanes CAPFT | ElectricEIRChiller McQuay WDC 1973kW/6.28COP/Vanes EIRFT | ElectricEIRChiller McQuay WDC 1973kW/6.28COP/Vanes EIRFPLR | .09 | 1.06 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 1997kW/7.24COP/Vanes | 1997400 | 7.24 | 8.89 | 26.67 | .04397 | .1041 | ElectricEIRChiller York YK 1997kW/7.24COP/Vanes CAPFT | ElectricEIRChiller York YK 1997kW/7.24COP/Vanes EIRFT | ElectricEIRChiller York YK 1997kW/7.24COP/Vanes EIRFPLR | .18 | 1.06 | 1.0 | .18 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PFH 2043kW/8.44COP/Vanes | 2043100 | 8.44 | 6.11 | 12.78 | .04757 | .06814 | ElectricEIRChiller McQuay PFH 2043kW/8.44COP/Vanes CAPFT | ElectricEIRChiller McQuay PFH 2043kW/8.44COP/Vanes EIRFT | ElectricEIRChiller McQuay PFH 2043kW/8.44COP/Vanes EIRFPLR | .08 | 1.02 | 1.0 | .08 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 2043kW/9.08COP/Vanes | 2043100 | 9.08 | 4.44 | 18.33 | .09085 | .11356 | ElectricEIRChiller Trane CVHF 2043kW/9.08COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 2043kW/9.08COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 2043kW/9.08COP/Vanes EIRFPLR | .28 | 1.04 | 1.0 | .28 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XL 2057kW/6.05COP/Vanes | 2057200 | 6.05 | 7.78 | 23.89 | .08322 | .09722 | ElectricEIRChiller Carrier 19XL 2057kW/6.05COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XL 2057kW/6.05COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XL 2057kW/6.05COP/Vanes EIRFPLR | .28 | 1.04 | 1.0 | .28 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 2110kW/7.15COP/Vanes | 2110000 | 7.15 | 7.22 | 23.89 | .06057 | .09464 | ElectricEIRChiller York YT 2110kW/7.15COP/Vanes CAPFT | ElectricEIRChiller York YT 2110kW/7.15COP/Vanes EIRFT | ElectricEIRChiller York YT 2110kW/7.15COP/Vanes EIRFPLR | .10 | 1.04 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PFH 2124kW/6.03COP/Vanes | 2124000 | 6.03 | 8.89 | 23.89 | .05552 | .07981 | ElectricEIRChiller McQuay PFH 2124kW/6.03COP/Vanes CAPFT | ElectricEIRChiller McQuay PFH 2124kW/6.03COP/Vanes EIRFT | ElectricEIRChiller McQuay PFH 2124kW/6.03COP/Vanes EIRFPLR | .09 | 1.03 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 2159kW/6.85COP/Vanes | 2159200 | 6.85 | 6.67 | 26.11 | .07571 | .11356 | ElectricEIRChiller York YK 2159kW/6.85COP/Vanes CAPFT | ElectricEIRChiller York YK 2159kW/6.85COP/Vanes EIRFT | ElectricEIRChiller York YK 2159kW/6.85COP/Vanes EIRFPLR | .14 | 1.05 | 1.0 | .14 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 2184kW/6.78COP/Vanes | 2183800 | 6.78 | 7.78 | 23.89 | .04883 | .05142 | ElectricEIRChiller Trane CVHF 2184kW/6.78COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 2184kW/6.78COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 2184kW/6.78COP/Vanes EIRFPLR | .09 | 1.01 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 2201kW/6.69COP/Vanes | 2201400 | 6.69 | 6.67 | 26.11 | .07571 | .11356 | ElectricEIRChiller York YK 2201kW/6.69COP/Vanes CAPFT | ElectricEIRChiller York YK 2201kW/6.69COP/Vanes EIRFT | ElectricEIRChiller York YK 2201kW/6.69COP/Vanes EIRFPLR | .14 | 1.05 | 1.0 | .14 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 2233kW/9.54COP/VSD | 2233000 | 9.54 | 5.56 | 12.78 | .06214 | .1164 | ElectricEIRChiller York YT 2233kW/9.54COP/VSD CAPFT | ElectricEIRChiller York YT 2233kW/9.54COP/VSD EIRFT | ElectricEIRChiller York YT 2233kW/9.54COP/VSD EIRFPLR | .10 | 1.04 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 2233kW/9.54COP/VSD | 2233000 | 9.54 | 5.56 | 12.78 | .06107 | .11451 | ElectricEIRChiller York YT 2233kW/9.54COP/VSD CAPFT | ElectricEIRChiller York YT 2233kW/9.54COP/VSD EIRFT | ElectricEIRChiller York YT 2233kW/9.54COP/VSD EIRFPLR | .10 | 1.04 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 2237kW/6.41COP/Vanes | 2236600 | 6.41 | 6.67 | 26.11 | .07571 | .11356 | ElectricEIRChiller York YK 2237kW/6.41COP/Vanes CAPFT | ElectricEIRChiller York YK 2237kW/6.41COP/Vanes EIRFT | ElectricEIRChiller York YK 2237kW/6.41COP/Vanes EIRFPLR | .13 | 1.01 | 1.0 | .13 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 2275kW/6.32COP/Vanes | 2275200 | 6.32 | 6.67 | 26.11 | .07571 | .11356 | ElectricEIRChiller York YK 2275kW/6.32COP/Vanes CAPFT | ElectricEIRChiller York YK 2275kW/6.32COP/Vanes EIRFT | ElectricEIRChiller York YK 2275kW/6.32COP/Vanes EIRFPLR | .13 | 1.02 | 1.0 | .13 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 2275kW/6.32COP/Vanes | 2275200 | 6.32 | 6.67 | 26.11 | .07571 | .11356 | ElectricEIRChiller York YK 2275kW/6.32COP/Vanes CAPFT | ElectricEIRChiller York YK 2275kW/6.32COP/Vanes EIRFT | ElectricEIRChiller York YK 2275kW/6.32COP/Vanes EIRFPLR | .13 | 1.03 | 1.0 | .13 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 2300kW/8.10COP/Vanes | 2299900 | 8.10 | 4.44 | 12.78 | .07571 | .09085 | ElectricEIRChiller Trane CVHF 2300kW/8.10COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 2300kW/8.10COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 2300kW/8.10COP/Vanes EIRFPLR | .23 | 1.02 | 1.0 | .23 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 2317kW/6.33COP/VSD | 2317400 | 6.33 | 5.56 | 29.44 | .09085 | .11356 | ElectricEIRChiller Trane CVHF 2317kW/6.33COP/VSD CAPFT | ElectricEIRChiller Trane CVHF 2317kW/6.33COP/VSD EIRFT | ElectricEIRChiller Trane CVHF 2317kW/6.33COP/VSD EIRFPLR | .10 | 1.04 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 2391kW/6.77COP/Vanes | 2391300 | 6.77 | 7.22 | 23.89 | .06858 | .0846 | ElectricEIRChiller Carrier 19XR 2391kW/6.77COP/Vanes CAPFT | ElectricEIRChiller Carrier 19XR 2391kW/6.77COP/Vanes EIRFT | ElectricEIRChiller Carrier 19XR 2391kW/6.77COP/Vanes EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19XR 2391kW/6.44COP/VSD | 2391300 | 6.44 | 7.22 | 23.89 | .06858 | .0846 | ElectricEIRChiller Carrier 19XR 2391kW/6.44COP/VSD CAPFT | ElectricEIRChiller Carrier 19XR 2391kW/6.44COP/VSD EIRFT | ElectricEIRChiller Carrier 19XR 2391kW/6.44COP/VSD EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 2412kW/5.58COP/Vanes | 2412400 | 5.58 | 6.67 | 26.11 | .09085 | .11356 | ElectricEIRChiller York YK 2412kW/5.58COP/Vanes CAPFT | ElectricEIRChiller York YK 2412kW/5.58COP/Vanes EIRFT | ElectricEIRChiller York YK 2412kW/5.58COP/Vanes EIRFPLR | .12 | 1.01 | 1.0 | .12 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PFH 2462kW/6.67COP/Vanes | 2461600 | 6.67 | 5.56 | 22.78 | .07066 | .10157 | ElectricEIRChiller McQuay PFH 2462kW/6.67COP/Vanes CAPFT | ElectricEIRChiller McQuay PFH 2462kW/6.67COP/Vanes EIRFT | ElectricEIRChiller McQuay PFH 2462kW/6.67COP/Vanes EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 2567kW/11.77COP/VSD | 2567100 | 11.77 | 4.44 | 12.78 | .12113 | .15142 | ElectricEIRChiller Trane CVHF 2567kW/11.77COP/VSD CAPFT | ElectricEIRChiller Trane CVHF 2567kW/11.77COP/VSD EIRFT | ElectricEIRChiller Trane CVHF 2567kW/11.77COP/VSD EIRFPLR | .11 | 1.04 | 1.0 | .11 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 2771kW/6.84COP/VSD | 2771100 | 6.84 | 5.56 | 23.89 | .10094 | .15142 | ElectricEIRChiller York YK 2771kW/6.84COP/VSD CAPFT | ElectricEIRChiller York YK 2771kW/6.84COP/VSD EIRFT | ElectricEIRChiller York YK 2771kW/6.84COP/VSD EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 2799kW/6.40COP/Vanes | 2799200 | 6.40 | 6.67 | 26.11 | .09893 | .13761 | ElectricEIRChiller Trane CVHF 2799kW/6.40COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 2799kW/6.40COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 2799kW/6.40COP/Vanes EIRFPLR | .20 | 1.04 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YT 3133kW/9.16COP/Vanes | 3133300 | 9.16 | 5.56 | 12.78 | .08076 | .12618 | ElectricEIRChiller York YT 3133kW/9.16COP/Vanes CAPFT | ElectricEIRChiller York YT 3133kW/9.16COP/Vanes EIRFT | ElectricEIRChiller York YT 3133kW/9.16COP/Vanes EIRFPLR | .07 | 1.03 | 1.0 | .07 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PFH 3165kW/6.48COP/Vanes | 3165000 | 6.48 | 5.56 | 22.78 | .09085 | .13627 | ElectricEIRChiller McQuay PFH 3165kW/6.48COP/Vanes CAPFT | ElectricEIRChiller McQuay PFH 3165kW/6.48COP/Vanes EIRFT | ElectricEIRChiller McQuay PFH 3165kW/6.48COP/Vanes EIRFPLR | .10 | 1.03 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller McQuay PFH 4020kW/7.35COP/Vanes | 4019500 | 7.35 | 6.67 | 12.78 | .07874 | .09842 | ElectricEIRChiller McQuay PFH 4020kW/7.35COP/Vanes CAPFT | ElectricEIRChiller McQuay PFH 4020kW/7.35COP/Vanes EIRFT | ElectricEIRChiller McQuay PFH 4020kW/7.35COP/Vanes EIRFPLR | .14 | 1.03 | 1.0 | .14 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 4396kW/6.63COP/Vanes | 4395800 | 6.63 | 6.67 | 26.67 | .19558 | .24605 | ElectricEIRChiller York YK 4396kW/6.63COP/Vanes CAPFT | ElectricEIRChiller York YK 4396kW/6.63COP/Vanes EIRFT | ElectricEIRChiller York YK 4396kW/6.63COP/Vanes EIRFPLR | .41 | 1.06 | 1.0 | .41 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 4477kW/6.64COP/Vanes | 4476700 | 6.64 | 6.67 | 26.67 | .19558 | .24605 | ElectricEIRChiller York YK 4477kW/6.64COP/Vanes CAPFT | ElectricEIRChiller York YK 4477kW/6.64COP/Vanes EIRFT | ElectricEIRChiller York YK 4477kW/6.64COP/Vanes EIRFPLR | .41 | 1.06 | 1.0 | .41 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 4515kW/6.22COP/Vanes | 4515400 | 6.22 | 6.67 | 26.67 | .19558 | .24605 | ElectricEIRChiller York YK 4515kW/6.22COP/Vanes CAPFT | ElectricEIRChiller York YK 4515kW/6.22COP/Vanes EIRFT | ElectricEIRChiller York YK 4515kW/6.22COP/Vanes EIRFPLR | .40 | 1.03 | 1.0 | .40 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 4537kW/6.28COP/Vanes | 4536500 | 6.28 | 6.67 | 26.67 | .19558 | .24605 | ElectricEIRChiller York YK 4537kW/6.28COP/Vanes CAPFT | ElectricEIRChiller York YK 4537kW/6.28COP/Vanes EIRFT | ElectricEIRChiller York YK 4537kW/6.28COP/Vanes EIRFPLR | .40 | 1.03 | 1.0 | .40 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 4610kW/6.34COP/Vanes | 4610300 | 6.34 | 6.67 | 26.11 | .19129 | .24757 | ElectricEIRChiller Trane CVHF 4610kW/6.34COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 4610kW/6.34COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 4610kW/6.34COP/Vanes EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19EX 4667kW/6.16COP/Vanes | 4666600 | 6.16 | 6.67 | 26.67 | .19558 | .24605 | ElectricEIRChiller Carrier 19EX 4667kW/6.16COP/Vanes CAPFT | ElectricEIRChiller Carrier 19EX 4667kW/6.16COP/Vanes EIRFT | ElectricEIRChiller Carrier 19EX 4667kW/6.16COP/Vanes EIRFPLR | .40 | 1.04 | 1.0 | .40 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CVHF 4677kW/6.27COP/Vanes | 4677100 | 6.27 | 6.67 | 26.67 | .20138 | .24605 | ElectricEIRChiller Trane CVHF 4677kW/6.27COP/Vanes CAPFT | ElectricEIRChiller Trane CVHF 4677kW/6.27COP/Vanes EIRFT | ElectricEIRChiller Trane CVHF 4677kW/6.27COP/Vanes EIRFPLR | .41 | 1.03 | 1.0 | .41 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 4966kW/6.05COP/Vanes | 4965500 | 6.05 | 6.67 | 26.11 | .21198 | .26498 | ElectricEIRChiller York YK 4966kW/6.05COP/Vanes CAPFT | ElectricEIRChiller York YK 4966kW/6.05COP/Vanes EIRFT | ElectricEIRChiller York YK 4966kW/6.05COP/Vanes EIRFPLR | .12 | 1.02 | 1.0 | .12 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 4969kW/7.14COP/Vanes | 4969000 | 7.14 | 6.67 | 26.11 | .17665 | .26498 | ElectricEIRChiller York YK 4969kW/7.14COP/Vanes CAPFT | ElectricEIRChiller York YK 4969kW/7.14COP/Vanes EIRFT | ElectricEIRChiller York YK 4969kW/7.14COP/Vanes EIRFPLR | .16 | 1.07 | 1.0 | .16 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 4969kW/7.07COP/Vanes | 4969000 | 7.07 | 6.67 | 26.11 | .17665 | .26498 | ElectricEIRChiller York YK 4969kW/7.07COP/Vanes CAPFT | ElectricEIRChiller York YK 4969kW/7.07COP/Vanes EIRFT | ElectricEIRChiller York YK 4969kW/7.07COP/Vanes EIRFPLR | .16 | 1.06 | 1.0 | .16 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19EX 4997kW/6.40COP/Vanes | 4997200 | 6.40 | 6.67 | 26.67 | .19558 | .24605 | ElectricEIRChiller Carrier 19EX 4997kW/6.40COP/Vanes CAPFT | ElectricEIRChiller Carrier 19EX 4997kW/6.40COP/Vanes EIRFT | ElectricEIRChiller Carrier 19EX 4997kW/6.40COP/Vanes EIRFPLR | .40 | 1.05 | 1.0 | .40 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19EX 5148kW/6.34COP/Vanes | 5148400 | 6.34 | 6.67 | 26.11 | .18283 | .25526 | ElectricEIRChiller Carrier 19EX 5148kW/6.34COP/Vanes CAPFT | ElectricEIRChiller Carrier 19EX 5148kW/6.34COP/Vanes EIRFT | ElectricEIRChiller Carrier 19EX 5148kW/6.34COP/Vanes EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 5170kW/7.15COP/Vanes | 5169500 | 7.15 | 6.67 | 26.11 | .17665 | .26498 | ElectricEIRChiller York YK 5170kW/7.15COP/Vanes CAPFT | ElectricEIRChiller York YK 5170kW/7.15COP/Vanes EIRFT | ElectricEIRChiller York YK 5170kW/7.15COP/Vanes EIRFPLR | .15 | 1.08 | 1.0 | .15 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19EX 5208kW/6.88COP/Vanes | 5208200 | 6.88 | 6.67 | 26.11 | .18283 | .25293 | ElectricEIRChiller Carrier 19EX 5208kW/6.88COP/Vanes CAPFT | ElectricEIRChiller Carrier 19EX 5208kW/6.88COP/Vanes EIRFT | ElectricEIRChiller Carrier 19EX 5208kW/6.88COP/Vanes EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 5465kW/6.94COP/Vanes | 5464900 | 6.94 | 6.67 | 26.11 | .18296 | .27444 | ElectricEIRChiller York YK 5465kW/6.94COP/Vanes CAPFT | ElectricEIRChiller York YK 5465kW/6.94COP/Vanes EIRFT | ElectricEIRChiller York YK 5465kW/6.94COP/Vanes EIRFPLR | .14 | 1.07 | 1.0 | .14 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YK 5549kW/6.50COP/Vanes | 5549300 | 6.50 | 6.67 | 26.11 | .18296 | .27444 | ElectricEIRChiller York YK 5549kW/6.50COP/Vanes CAPFT | ElectricEIRChiller York YK 5549kW/6.50COP/Vanes EIRFT | ElectricEIRChiller York YK 5549kW/6.50COP/Vanes EIRFPLR | .14 | 1.05 | 1.0 | .14 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 19FA 5651kW/5.50COP/Vanes | 5651300 | 5.50 | 6.67 | 29.44 | .18927 | .18927 | ElectricEIRChiller Carrier 19FA 5651kW/5.50COP/Vanes CAPFT | ElectricEIRChiller Carrier 19FA 5651kW/5.50COP/Vanes EIRFT | ElectricEIRChiller Carrier 19FA 5651kW/5.50COP/Vanes EIRFPLR | .19 | 1.02 | 1.0 | .19 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
DOE-2 Centrifugal/5.50COP | Autosize | 5.5 | 6.67 | 29.4 | Autosize | Autosize | DOE-2 Centrifugal/5.50COP CAPFT | DOE-2 Centrifugal/5.50COP EIRFT | DOE-2 Centrifugal/5.50COP EIRFPLR | 0.1 | 1.0 | 1.0 | 0.2 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow
ElectricEIRChiller Multistack MS 172kW/3.67COP/None | 172300 | 3.67 | 4.44 | 18.33 | .00738 | .00959 | ElectricEIRChiller Multistack MS 172kW/3.67COP/None CAPFT | ElectricEIRChiller Multistack MS 172kW/3.67COP/None EIRFT | ElectricEIRChiller Multistack MS 172kW/3.67COP/None EIRFPLR | .40 | 1.03 | 1.0 | .40 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
DOE-2 Reciprocating/3.67COP | Autosize | 3.67 | 6.67 | 29.4 | Autosize | Autosize | DOE-2 Reciprocating/3.67COP CAPFT | DOE-2 Reciprocating/3.67COP EIRFT | DOE-2 Reciprocating/3.67COP EIRFPLR | 0.1 | 1.0 | 1.0 | 0.2 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow
ElectricEIRChiller Trane RTWA 383kW/4.17COP/Valve | 383300 | 4.17 | 6.67 | 29.44 | .0165 | .02063 | ElectricEIRChiller Trane RTWA 383kW/4.17COP/Valve CAPFT | ElectricEIRChiller Trane RTWA 383kW/4.17COP/Valve EIRFT | ElectricEIRChiller Trane RTWA 383kW/4.17COP/Valve EIRFPLR | .25 | 1.01 | 1.0 | .25 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane RTHB 531kW/4.83COP/Valve | 531000 | 4.83 | 5.56 | 23.89 | .0135 | .01577 | ElectricEIRChiller Trane RTHB 531kW/4.83COP/Valve CAPFT | ElectricEIRChiller Trane RTHB 531kW/4.83COP/Valve EIRFT | ElectricEIRChiller Trane RTHB 531kW/4.83COP/Valve EIRFPLR | .30 | 1.01 | 1.0 | .30 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane RTHB 538kW/5.12COP/Valve | 538000 | 5.12 | 5.56 | 23.89 | .01375 | .01956 | ElectricEIRChiller Trane RTHB 538kW/5.12COP/Valve CAPFT | ElectricEIRChiller Trane RTHB 538kW/5.12COP/Valve EIRFT | ElectricEIRChiller Trane RTHB 538kW/5.12COP/Valve EIRFPLR | .30 | 1.01 | 1.0 | .30 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane RTHB 542kW/5.26COP/Valve | 541500 | 5.26 | 5.56 | 21.11 | .01363 | .01577 | ElectricEIRChiller Trane RTHB 542kW/5.26COP/Valve CAPFT | ElectricEIRChiller Trane RTHB 542kW/5.26COP/Valve EIRFT | ElectricEIRChiller Trane RTHB 542kW/5.26COP/Valve EIRFPLR | .30 | 1.01 | 1.0 | .30 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YS 672kW/7.90COP/Valve | 671600 | 7.90 | 6.11 | 15.56 | .01514 | .0241 | ElectricEIRChiller York YS 672kW/7.90COP/Valve CAPFT | ElectricEIRChiller York YS 672kW/7.90COP/Valve EIRFT | ElectricEIRChiller York YS 672kW/7.90COP/Valve EIRFPLR | .09 | 1.01 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 23XL 686kW/5.91COP/Valve | 685700 | 5.91 | 6.11 | 23.74 | .0571 | .03255 | ElectricEIRChiller Carrier 23XL 686kW/5.91COP/Valve CAPFT | ElectricEIRChiller Carrier 23XL 686kW/5.91COP/Valve EIRFT | ElectricEIRChiller Carrier 23XL 686kW/5.91COP/Valve EIRFPLR | .20 | 1.04 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane RTHC 707kW/7.77COP/Valve | 706800 | 7.77 | 5.56 | 15.56 | .04921 | .03268 | ElectricEIRChiller Trane RTHC 707kW/7.77COP/Valve CAPFT | ElectricEIRChiller Trane RTHC 707kW/7.77COP/Valve EIRFT | ElectricEIRChiller Trane RTHC 707kW/7.77COP/Valve EIRFPLR | .28 | 1.01 | 1.0 | .28 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YS 756kW/7.41COP/Valve | 756000 | 7.41 | 5.56 | 16.06 | .06782 | .05142 | ElectricEIRChiller York YS 756kW/7.41COP/Valve CAPFT | ElectricEIRChiller York YS 756kW/7.41COP/Valve EIRFT | ElectricEIRChiller York YS 756kW/7.41COP/Valve EIRFPLR | .11 | 1.01 | 1.0 | .11 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YS 781kW/5.42COP/Valve | 780700 | 5.42 | 6.67 | 29.44 | .01893 | .03785 | ElectricEIRChiller York YS 781kW/5.42COP/Valve CAPFT | ElectricEIRChiller York YS 781kW/5.42COP/Valve EIRFT | ElectricEIRChiller York YS 781kW/5.42COP/Valve EIRFPLR | .09 | 1.01 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 23XL 830kW/6.97COP/Valve | 829900 | 6.97 | 5.56 | 23.89 | .03186 | .04744 | ElectricEIRChiller Carrier 23XL 830kW/6.97COP/Valve CAPFT | ElectricEIRChiller Carrier 23XL 830kW/6.97COP/Valve EIRFT | ElectricEIRChiller Carrier 23XL 830kW/6.97COP/Valve EIRFPLR | .20 | 1.01 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 23XL 862kW/6.11COP/Valve | 861500 | 6.11 | 6.67 | 23.89 | .06782 | .04296 | ElectricEIRChiller Carrier 23XL 862kW/6.11COP/Valve CAPFT | ElectricEIRChiller Carrier 23XL 862kW/6.11COP/Valve EIRFT | ElectricEIRChiller Carrier 23XL 862kW/6.11COP/Valve EIRFPLR | .20 | 1.04 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 23XL 862kW/6.84COP/Valve | 861500 | 6.84 | 9.69 | 23.89 | .06782 | .04296 | ElectricEIRChiller Carrier 23XL 862kW/6.84COP/Valve CAPFT | ElectricEIRChiller Carrier 23XL 862kW/6.84COP/Valve EIRFT | ElectricEIRChiller Carrier 23XL 862kW/6.84COP/Valve EIRFPLR | .30 | 1.04 | 1.0 | .30 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 23XL 865kW/6.05COP/Valve | 865100 | 6.05 | 4.44 | 26.11 | .03716 | .04366 | ElectricEIRChiller Carrier 23XL 865kW/6.05COP/Valve CAPFT | ElectricEIRChiller Carrier 23XL 865kW/6.05COP/Valve EIRFT | ElectricEIRChiller Carrier 23XL 865kW/6.05COP/Valve EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YS 879kW/5.82COP/Valve | 879100 | 5.82 | 4.44 | 26.11 | .03785 | .04732 | ElectricEIRChiller York YS 879kW/5.82COP/Valve CAPFT | ElectricEIRChiller York YS 879kW/5.82COP/Valve EIRFT | ElectricEIRChiller York YS 879kW/5.82COP/Valve EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane RTHC 1009kW/5.37COP/Valve | 1009200 | 5.37 | 5.56 | 24.86 | .03186 | .04618 | ElectricEIRChiller Trane RTHC 1009kW/5.37COP/Valve CAPFT | ElectricEIRChiller Trane RTHC 1009kW/5.37COP/Valve EIRFT | ElectricEIRChiller Trane RTHC 1009kW/5.37COP/Valve EIRFPLR | .30 | 1.01 | 1.0 | .30 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane RTHB 1051kW/5.05COP/Valve | 1051400 | 5.05 | 6.67 | 29.44 | .04527 | .05659 | ElectricEIRChiller Trane RTHB 1051kW/5.05COP/Valve CAPFT | ElectricEIRChiller Trane RTHB 1051kW/5.05COP/Valve EIRFT | ElectricEIRChiller Trane RTHB 1051kW/5.05COP/Valve EIRFPLR | .20 | 1.01 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 23XL 1062kW/5.50COP/Valve | 1062000 | 5.50 | 6.67 | 29.44 | .04573 | .05716 | ElectricEIRChiller Carrier 23XL 1062kW/5.50COP/Valve CAPFT | ElectricEIRChiller Carrier 23XL 1062kW/5.50COP/Valve EIRFT | ElectricEIRChiller Carrier 23XL 1062kW/5.50COP/Valve EIRFPLR | .20 | 1.01 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane RTHC 1066kW/5.73COP/Valve | 1065500 | 5.73 | 5.56 | 25.28 | .05142 | .04416 | ElectricEIRChiller Trane RTHC 1066kW/5.73COP/Valve CAPFT | ElectricEIRChiller Trane RTHC 1066kW/5.73COP/Valve EIRFT | ElectricEIRChiller Trane RTHC 1066kW/5.73COP/Valve EIRFPLR | .30 | 1.01 | 1.0 | .30 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane RTHC 1094kW/6.55COP/Valve | 1093600 | 6.55 | 5.56 | 23.33 | .04921 | .04524 | ElectricEIRChiller Trane RTHC 1094kW/6.55COP/Valve CAPFT | ElectricEIRChiller Trane RTHC 1094kW/6.55COP/Valve EIRFT | ElectricEIRChiller Trane RTHC 1094kW/6.55COP/Valve EIRFPLR | .25 | 1.01 | 1.0 | .25 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 23XL 1108kW/6.92COP/Valve | 1107700 | 6.92 | 8.97 | 23.74 | .0571 | .05142 | ElectricEIRChiller Carrier 23XL 1108kW/6.92COP/Valve CAPFT | ElectricEIRChiller Carrier 23XL 1108kW/6.92COP/Valve EIRFT | ElectricEIRChiller Carrier 23XL 1108kW/6.92COP/Valve EIRFPLR | .20 | 1.02 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YS 1171kW/9.15COP/Valve | 1171000 | 9.15 | 6.11 | 15.56 | .03249 | .05173 | ElectricEIRChiller York YS 1171kW/9.15COP/Valve CAPFT | ElectricEIRChiller York YS 1171kW/9.15COP/Valve EIRFT | ElectricEIRChiller York YS 1171kW/9.15COP/Valve EIRFPLR | .09 | 1.01 | 1.0 | .09 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Carrier 23XL 1196kW/6.39COP/Valve | 1195600 | 6.39 | 7.22 | 23.89 | .03653 | .04271 | ElectricEIRChiller Carrier 23XL 1196kW/6.39COP/Valve CAPFT | ElectricEIRChiller Carrier 23XL 1196kW/6.39COP/Valve EIRFT | ElectricEIRChiller Carrier 23XL 1196kW/6.39COP/Valve EIRFPLR | .20 | 1.03 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YS 1554kW/9.31COP/Valve | 1554300 | 9.31 | 5.56 | 15.56 | .0424 | .07949 | ElectricEIRChiller York YS 1554kW/9.31COP/Valve CAPFT | ElectricEIRChiller York YS 1554kW/9.31COP/Valve EIRFT | ElectricEIRChiller York YS 1554kW/9.31COP/Valve EIRFPLR | .10 | 1.02 | 1.0 | .10 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller York YS 1758kW/5.84COP/Valve | 1758300 | 5.84 | 6.67 | 29.44 | .07571 | .09464 | ElectricEIRChiller York YS 1758kW/5.84COP/Valve CAPFT | ElectricEIRChiller York YS 1758kW/5.84COP/Valve EIRFT | ElectricEIRChiller York YS 1758kW/5.84COP/Valve EIRFPLR | .20 | 1.04 | 1.0 | .20 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0
ElectricEIRChiller Trane CGWD 207kW/3.99COP/None | 207400 | 3.99 | 6.67 | 29.44 | .00898 | .01122 | ElectricEIRChiller Trane CGWD 207kW/3.99COP/None CAPFT | ElectricEIRChiller Trane CGWD 207kW/3.99COP/None EIRFT | ElectricEIRChiller Trane CGWD 207kW/3.99COP/None EIRFPLR | .25 | 1.01 | 1.0 | .25 | Chilled Water Side Inlet Node | Chilled Water Side Outlet Node | Condenser Side Inlet Node | Condenser Side Outlet Node | WATER COOLED |  | 1.0 | 2.0 | ConstantFlow | 0.0

## CURVE BIQUADRATIC CAPFT
Name | Coeff1 Constant | Coeff2 x | Coeff3 x**2 | Coeff4 y | Coeff5 y**2 | Coeff6 x*y | minimum value of x | maximum value of x | minimum value of y | maximum value of y
Curve名称 | 常数项C1 | x系数C2 | X2系数C3 | y系数C4 | y2系数C5 | xy系数C6 | x的最小值 | x的最大值 | y的最小值 | y的最大值
系数
ElectricEIRChiller McQuay WSC 471kW/5.89COP/Vanes CAPFT | 2.521130E-01 | 1.324053E-02 | -8.637329E-03 | 8.581056E-02 | -4.261176E-03 | 8.661899E-03 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller York YT 563kW/10.61COP/Vanes CAPFT | -1.288612E-01 | -8.919540E-02 | -2.190195E-03 | 1.538357E-01 | -5.129402E-03 | 7.813636E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller McQuay PEH 703kW/7.03COP/Vanes CAPFT | 4.779439E-01 | 1.073486E-01 | -1.055896E-02 | 4.208433E-02 | -2.346870E-03 | 4.019632E-03 | 5.56 | 8.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 23XL 724kW/6.04COP/Vanes CAPFT | 4.418712E-01 | -8.384251E-02 | -2.190707E-03 | 8.594633E-02 | -3.322575E-03 | 6.652189E-03 | 5.56 | 10.00 | 13.75 | 23.89
ElectricEIRChiller Carrier 19XR 742kW/5.42COP/VSD CAPFT | 9.797101E-01 | -2.895701E-03 | -8.970718E-04 | 1.031440E-02 | -7.431651E-04 | 1.453508E-03 | 5.56 | 10.00 | 11.25 | 23.89
ElectricEIRChiller McQuay WSC 816kW/6.74COP/Vanes CAPFT | 9.862590E-01 | 5.799373E-02 | -5.355626E-03 | -8.941705E-04 | -1.670098E-03 | 4.733054E-03 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller McQuay PEH 819kW/8.11COP/Vanes CAPFT | 7.392673E-01 | 4.328784E-02 | -4.529446E-03 | 1.525410E-02 | -1.141458E-03 | 2.651124E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XR 823kW/6.28COP/Vanes CAPFT | 5.573150E-01 | 8.714616E-02 | -2.917582E-03 | 2.500000E-02 | -8.861538E-04 | -3.184615E-04 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 869kW/5.57COP/VSD CAPFT | 5.406799E-01 | 1.253709E-01 | -8.025360E-03 | -7.357554E-03 | -4.477789E-04 | 2.140733E-03 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 897kW/7.23COP/VSD CAPFT | 5.559679E-01 | 7.630860E-02 | -1.431181E-03 | 2.167593E-02 | -6.233447E-04 | -9.876498E-04 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 897kW/6.50COP/Vanes CAPFT | 7.009156E-01 | 2.151274E-02 | -6.029650E-04 | 1.864266E-02 | -1.084545E-03 | 1.418575E-03 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller York YT 897kW/7.60COP/VSD CAPFT | 5.699948E-01 | 2.961470E-02 | -1.064930E-03 | 3.062313E-02 | -1.753205E-03 | 2.142105E-03 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller York YT 897kW/6.27COP/VSD CAPFT | 1.197991E-01 | 1.568955E-01 | -4.426242E-03 | 3.449640E-02 | -8.163597E-04 | -2.236230E-03 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 897kW/6.23COP/VSD CAPFT | 8.862185E-01 | 3.144947E-02 | 2.328997E-04 | 1.339712E-03 | -2.923430E-04 | 2.320709E-04 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller McQuay PFH 932kW/5.09COP/Vanes CAPFT | 1.182278E+00 | 3.259490E-02 | -3.904288E-03 | 4.579721E-03 | -1.028178E-03 | 2.855063E-03 | 3.33 | 7.78 | 12.78 | 29.44
ElectricEIRChiller York YT 960kW/4.64COP/Vanes CAPFT | -2.278537E-01 | 4.055945E-01 | -3.246694E-02 | 3.788230E-03 | -2.236584E-04 | 6.715520E-04 | 3.33 | 7.78 | 12.78 | 29.44
ElectricEIRChiller York YT 1023kW/5.81COP/Vanes CAPFT | 2.571195E-01 | -1.571421E-02 | -3.041761E-03 | 8.106512E-02 | -2.568598E-03 | 4.247073E-03 | 4.44 | 8.89 | 12.78 | 35.00
ElectricEIRChiller McQuay PEH 1030kW/8.58COP/Vanes CAPFT | 7.736028E-01 | 5.571395E-02 | -3.058312E-03 | -1.789007E-04 | -9.808878E-04 | 2.123462E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller York YT 1048kW/6.06COP/Vanes CAPFT | 7.238221E-01 | 1.747548E-02 | -4.524718E-03 | 2.138468E-02 | -9.342801E-04 | 2.515069E-03 | 4.44 | 8.89 | 15.56 | 35.00
ElectricEIRChiller York YT 1055kW/5.96COP/Vanes CAPFT | 1.785912E-01 | -5.900023E-02 | -5.946963E-04 | 9.297889E-02 | -2.841024E-03 | 4.974221E-03 | 4.44 | 8.89 | 12.78 | 35.00
ElectricEIRChiller Carrier 19XR 1076kW/5.52COP/Vanes CAPFT | 9.187704E-01 | 4.509452E-02 | -5.119187E-03 | -2.095629E-04 | -6.432511E-04 | 2.791545E-03 | 5.56 | 10.00 | 12.78 | 24.89
ElectricEIRChiller Trane CVHE 1080kW/7.39COP/Vanes CAPFT | 4.365583E-01 | -3.677215E-02 | -2.779781E-03 | 6.063060E-02 | -2.290704E-03 | 5.115883E-03 | 5.56 | 10.00 | 16.24 | 23.61
ElectricEIRChiller York YT 1090kW/7.57COP/VSD CAPFT | 6.769028E-01 | 5.711844E-02 | -6.072310E-04 | 1.656541E-02 | -8.087831E-04 | 2.303904E-04 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller McQuay PEH 1104kW/8.00COP/Vanes CAPFT | 8.210185E-01 | 4.386152E-02 | -1.521829E-03 | -4.314921E-03 | -7.251667E-04 | 1.497681E-03 | 6.67 | 12.22 | 12.78 | 23.89
ElectricEIRChiller York YT 1125kW/7.92COP/VSD CAPFT | 1.034212E-01 | 2.327078E-03 | -9.117035E-04 | 9.104793E-02 | -2.678967E-03 | 2.274649E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller Trane CVHE 1125kW/4.89COP/Vanes CAPFT | 6.151549E-01 | -1.181250E-02 | -1.491630E-03 | 3.326625E-02 | -9.315000E-04 | 1.771875E-03 | 5.56 | 10.00 | 15.56 | 23.89
ElectricEIRChiller York YT 1125kW/7.92COP/VSD CAPFT | 1.034212E-01 | 2.327078E-03 | -9.117035E-04 | 9.104793E-02 | -2.678967E-03 | 2.274649E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller Trane CVHE 1129kW/7.19COP/Vanes CAPFT | 3.922479E-01 | -4.388411E-02 | -2.748665E-03 | 6.894954E-02 | -2.563738E-03 | 5.420187E-03 | 5.56 | 10.00 | 15.56 | 23.89
ElectricEIRChiller Carrier 19XR 1143kW/6.57COP/VSD CAPFT | 7.939538E-01 | 4.096493E-02 | -1.419397E-03 | -1.639813E-03 | -5.220497E-04 | 1.348786E-03 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 1157kW/5.62COP/VSD CAPFT | 1.076248E+00 | 5.436724E-03 | -3.893302E-04 | -4.353310E-03 | -2.402031E-04 | 8.409080E-04 | 5.56 | 10.00 | 11.25 | 23.89
ElectricEIRChiller Carrier 19XR 1196kW/6.50COP/Vanes CAPFT | 1.126801E+00 | -4.220591E-03 | -2.002964E-03 | 7.360880E-03 | -1.156890E-03 | 3.064875E-03 | 6.67 | 12.22 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1213kW/7.78COP/Vanes CAPFT | 9.070437E-01 | -7.437456E-03 | -9.695325E-04 | 1.529092E-02 | -1.069664E-03 | 1.994583E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller McQuay PEH 1231kW/6.18COP/Vanes CAPFT | 1.152795E+00 | 9.770474E-02 | -6.719705E-03 | -2.123401E-02 | -3.641998E-04 | 1.473439E-03 | 5.56 | 8.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1234kW/5.39COP/VSD CAPFT | 5.905815E-01 | 1.190927E-01 | -6.727309E-03 | -9.580836E-03 | -3.034704E-04 | 1.540686E-03 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 1259kW/6.26COP/Vanes CAPFT | 1.082071E+00 | 3.200888E-02 | -3.994780E-03 | -5.789604E-03 | -8.238938E-04 | 2.933539E-03 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller York YK 1259kW/6.45COP/Vanes CAPFT | 9.609200E-01 | 7.223733E-02 | -1.693471E-03 | 2.543722E-03 | -6.415570E-04 | -3.028540E-04 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller York YT 1266kW/4.39COP/Vanes CAPFT | 1.285663E-01 | -2.860032E-02 | -1.369319E-03 | 6.676366E-02 | -1.510647E-03 | 2.947167E-03 | 5.56 | 8.89 | 12.78 | 35.00
ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes CAPFT | 1.119245E+00 | -1.524417E-02 | -1.074186E-03 | -1.260169E-03 | -4.380237E-04 | 2.027779E-03 | 5.56 | 8.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes CAPFT | 1.119245E+00 | -1.524417E-02 | -1.074186E-03 | -1.260169E-03 | -4.380237E-04 | 2.027779E-03 | 5.56 | 8.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1294kW/7.61COP/Vanes CAPFT | 9.274222E-01 | 1.278683E-02 | -1.621880E-03 | 2.816339E-03 | -7.658105E-04 | 1.881968E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller Trane CVHE 1329kW/5.38COP/Vanes CAPFT | 5.339754E-01 | 1.016009E-01 | -3.979592E-03 | 1.261254E-02 | -4.666667E-04 | -8.351648E-05 | 6.11 | 10.00 | 21.11 | 29.44
ElectricEIRChiller Carrier 19XR 1350kW/7.90COP/VSD CAPFT | 1.063866E+00 | -1.448990E-02 | -1.021036E-03 | -1.197817E-03 | -4.163507E-04 | 1.927446E-03 | 5.56 | 8.89 | 12.78 | 23.89
ElectricEIRChiller York YT 1368kW/7.35COP/VSD CAPFT | 3.832184E-01 | -3.265439E-02 | -3.392654E-03 | 8.580180E-02 | -3.513013E-03 | 6.528440E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Trane CVHE 1372kW/7.49COP/Vanes CAPFT | 5.993784E-01 | 6.523380E-02 | -7.714286E-03 | 3.114955E-02 | -1.843989E-03 | 4.096552E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YT 1396kW/7.35COP/Vanes CAPFT | 5.167863E-01 | -2.788454E-02 | -9.497810E-04 | 6.693411E-02 | -2.728430E-03 | 4.723123E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XR 1403kW/7.09COP/VSD CAPFT | 9.601814E-01 | -3.596494E-03 | -1.706786E-03 | 6.272429E-03 | -9.858212E-04 | 2.611673E-03 | 6.67 | 12.22 | 12.78 | 23.89
ElectricEIRChiller York YT 1403kW/6.94COP/VSD CAPFT | -3.447077E-02 | 1.273138E-01 | -9.716868E-03 | 8.863546E-02 | -3.165958E-03 | 2.521351E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Trane CVHE 1407kW/7.14COP/VSD CAPFT | 4.521342E-01 | 5.248142E-03 | -6.687636E-03 | 5.869437E-02 | -2.390647E-03 | 5.040171E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller McQuay PFH 1407kW/6.60COP/Vanes CAPFT | 1.191784E+00 | 2.070584E-02 | -4.952378E-03 | 1.757508E-02 | -2.487599E-03 | 5.934709E-03 | 5.56 | 8.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1407kW/6.04COP/VSD CAPFT | 1.042261E+00 | 2.644821E-03 | -1.468026E-03 | 1.366256E-02 | -8.302334E-04 | 1.573579E-03 | 4.44 | 10.00 | 12.78 | 32.22
ElectricEIRChiller Carrier 19XR 1410kW/8.54COP/VSD CAPFT | 9.597856E-01 | -6.247187E-03 | -1.117998E-03 | 6.991040E-03 | -6.321252E-04 | 1.765068E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller Trane CVHE 1442kW/6.61COP/VSD CAPFT | 4.007341E-01 | 1.148568E-03 | 1.049504E-04 | 5.574667E-02 | -1.646131E-03 | 1.323200E-03 | 4.44 | 8.89 | 12.78 | 35.00
ElectricEIRChiller York YT 1459kW/6.40COP/VSD CAPFT | -1.665585E-01 | 2.211580E-01 | -1.408361E-02 | 6.476151E-02 | -2.009341E-03 | -7.897630E-05 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Trane CVHE 1484kW/9.96COP/VSD CAPFT | -4.544480E-01 | -3.615933E-02 | -2.734006E-03 | 1.683863E-01 | -4.557649E-03 | 5.362840E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YT 1495kW/7.51COP/VSD CAPFT | 1.051921E+00 | -1.632255E-01 | 1.149042E-02 | 5.463515E-02 | -1.579985E-03 | 1.628246E-03 | 5.56 | 8.89 | 12.78 | 35.00
ElectricEIRChiller McQuay WSC 1519kW/7.10COP/Vanes CAPFT | 1.265889E+00 | 3.401563E-02 | -6.532621E-03 | -6.600960E-03 | -2.172017E-03 | 7.121766E-03 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 1558kW/5.81COP/VSD CAPFT | 1.034307E+00 | 2.390635E-02 | -1.222578E-03 | -5.346220E-03 | -2.183258E-04 | 6.282331E-04 | 5.56 | 10.00 | 11.94 | 23.89
ElectricEIRChiller Carrier 19XR 1586kW/5.53COP/VSD CAPFT | 1.119233E+00 | 1.130501E-02 | -6.423802E-04 | -5.144512E-03 | -3.085995E-04 | 7.813582E-04 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller McQuay PEH 1635kW/7.47COP/Vanes CAPFT | 9.894188E-01 | 2.983148E-03 | -2.484601E-03 | 5.974984E-03 | -1.063988E-03 | 2.601503E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XR 1635kW/6.36COP/Vanes CAPFT | 7.639212E-01 | 1.160405E-02 | -5.344185E-03 | 3.306796E-02 | -2.100827E-03 | 4.920586E-03 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 1656kW/8.24COP/VSD CAPFT | 7.611706E-01 | -2.867067E-02 | -2.363358E-03 | 4.097113E-02 | -2.343044E-03 | 4.547017E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller York YT 1663kW/9.34COP/Vanes CAPFT | 9.112226E-01 | -4.546497E-02 | 4.431126E-03 | 2.439160E-02 | -1.415836E-03 | 1.877877E-03 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XL 1674kW/7.89COP/Vanes CAPFT | 2.925408E-01 | -4.406182E-02 | -1.292074E-03 | 9.008701E-02 | -2.646719E-03 | 3.388396E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Trane CVHF 1681kW/6.59COP/Vanes CAPFT | 6.792987E-01 | -5.291217E-02 | -5.280108E-03 | 5.252682E-02 | -2.523689E-03 | 7.344940E-03 | 5.56 | 10.00 | 18.33 | 23.89
ElectricEIRChiller Carrier 19XR 1723kW/8.32COP/VSD CAPFT | 4.742518E-01 | -5.109937E-02 | -2.845323E-03 | 8.257997E-02 | -3.404799E-03 | 5.625321E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1727kW/9.04COP/Vanes CAPFT | 6.509915E-01 | 2.567642E-02 | -5.417815E-03 | 3.406103E-02 | -1.703640E-03 | 3.336164E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller McQuay WSC 1751kW/6.73COP/Vanes CAPFT | 7.923045E-01 | 1.003672E-01 | -4.348900E-03 | 3.755572E-03 | -7.675491E-04 | 6.788600E-04 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller Trane CVHF 1758kW/5.96COP/Vanes CAPFT | 1.074211E+00 | 7.710761E-03 | -3.166770E-03 | -1.868765E-02 | 1.273866E-04 | 2.744586E-03 | 5.56 | 10.00 | 12.78 | 24.44
ElectricEIRChiller York YT 1758kW/5.76COP/VSD CAPFT | 4.575085E-01 | 1.313508E-01 | -4.408831E-03 | 1.930354E-02 | -5.479641E-04 | -1.376580E-03 | 5.56 | 10.51 | 12.78 | 24.44
ElectricEIRChiller York YT 1758kW/6.26COP/Vanes CAPFT | 8.975936E-01 | -1.459740E-02 | 3.647187E-03 | 3.202545E-02 | -1.190379E-03 | 3.297810E-04 | 5.56 | 10.00 | 12.78 | 24.44
ElectricEIRChiller York YT 1758kW/5.96COP/Vanes CAPFT | 8.492365E-01 | 5.551947E-02 | -2.973138E-04 | 1.164389E-03 | -2.955716E-04 | 8.464931E-05 | 5.56 | 10.00 | 12.78 | 24.44
ElectricEIRChiller Trane CVHE 1758kW/5.96COP/Vanes CAPFT | 9.566057E-02 | -2.457943E-02 | -6.827143E-03 | 7.119360E-02 | -2.047680E-03 | 5.248800E-03 | 4.44 | 8.89 | 23.89 | 35.00
ElectricEIRChiller York YT 1758kW/6.28COP/Vanes CAPFT | 7.079149E-01 | -2.006276E-03 | -2.596043E-03 | 3.005922E-02 | -1.056423E-03 | 2.045705E-03 | 4.44 | 8.89 | 15.56 | 35.00
ElectricEIRChiller Carrier 19XR 1758kW/5.86COP/VSD CAPFT | 3.677279E-01 | -3.175504E-02 | -4.096383E-03 | 7.527566E-02 | -2.757540E-03 | 5.359020E-03 | 5.56 | 10.00 | 12.78 | 24.44
ElectricEIRChiller Trane CVHF 1758kW/6.46COP/VSD CAPFT | 1.066671E+00 | 5.889240E-03 | -3.155053E-03 | -1.591039E-02 | 1.042897E-04 | 2.576256E-03 | 5.56 | 10.00 | 12.78 | 24.44
ElectricEIRChiller Trane CVHF 1758kW/6.87COP/Vanes CAPFT | 8.085529E-01 | 3.412026E-02 | -4.184591E-04 | 4.111323E-03 | -1.764627E-04 | 4.184748E-04 | 5.56 | 10.00 | 12.78 | 24.44
ElectricEIRChiller Carrier 19XR 1776kW/8.00COP/Vanes CAPFT | 4.841535E-01 | -3.584260E-02 | -1.467417E-03 | 7.773868E-02 | -3.125809E-03 | 3.729631E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XL 1779kW/6.18COP/Vanes CAPFT | 2.703515E-01 | -4.051337E-02 | -5.968813E-03 | 8.261488E-02 | -3.019425E-03 | 6.718040E-03 | 4.44 | 8.89 | 15.56 | 26.11
ElectricEIRChiller Trane CVHF 1779kW/6.18COP/Vanes CAPFT | 3.331346E-01 | -5.678656E-02 | -1.257764E-03 | 8.198893E-02 | -2.612490E-03 | 4.226087E-03 | 5.56 | 10.00 | 18.33 | 23.89
ElectricEIRChiller York YT 1794kW/8.11COP/Vanes CAPFT | 1.536140E+00 | -1.630760E-01 | 1.225832E-02 | 2.148166E-02 | -1.654700E-03 | 2.660568E-03 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YT 1794kW/7.90COP/VSD CAPFT | 9.552268E-01 | -1.553435E-01 | 7.958834E-03 | 6.132388E-02 | -1.899594E-03 | 3.323245E-03 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XL 1797kW/5.69COP/Vanes CAPFT | 9.084596E-01 | 4.671596E-02 | -1.188845E-03 | -2.284596E-03 | -3.170254E-05 | -3.577858E-04 | 6.67 | 10.00 | 21.11 | 29.44
ElectricEIRChiller Carrier 19XR 1801kW/6.34COP/VSD CAPFT | 6.174861E-01 | -7.299051E-02 | -1.897105E-03 | 7.003662E-02 | -2.852439E-03 | 5.751931E-03 | 6.67 | 12.22 | 12.78 | 23.89
ElectricEIRChiller York YT 1867kW/10.09COP/Vanes CAPFT | 4.451516E-01 | -1.252382E-02 | -2.878042E-03 | 6.132233E-02 | -2.365055E-03 | 4.514258E-03 | 4.44 | 8.89 | 12.78 | 35.00
ElectricEIRChiller Carrier 19XL 1871kW/6.49COP/Vanes CAPFT | 5.658630E-03 | -3.836575E-02 | -5.122195E-03 | 1.068063E-01 | -3.377824E-03 | 5.650118E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller York YT 1881kW/6.77COP/VSD CAPFT | 5.065247E-01 | -4.158206E-03 | -2.681976E-03 | 4.763436E-02 | -1.951270E-03 | 3.994399E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YK 1881kW/6.53COP/Vanes CAPFT | 8.561286E-01 | 4.130164E-02 | -7.109335E-04 | 4.306273E-03 | -6.336613E-04 | 7.211635E-04 | 7.22 | 12.78 | 9.44 | 26.67
ElectricEIRChiller York YK 1881kW/6.53COP/Vanes CAPFT | 8.561286E-01 | 4.130164E-02 | -7.109335E-04 | 4.306273E-03 | -6.336613E-04 | 7.211635E-04 | 7.22 | 12.78 | 9.44 | 26.67
ElectricEIRChiller McQuay PEH 1895kW/6.42COP/Vanes CAPFT | 8.573195E-01 | -1.131937E-01 | 3.444205E-03 | 4.865045E-02 | -2.103805E-03 | 4.986639E-03 | 4.44 | 8.89 | 12.78 | 35.00
ElectricEIRChiller York YT 1934kW/7.55COP/Vanes CAPFT | 4.420318E-02 | 1.103599E-01 | -2.597752E-03 | 7.043754E-02 | -2.138316E-03 | -4.696924E-04 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller McQuay PEH 1934kW/6.01COP/Vanes CAPFT | 2.893111E-01 | -3.834949E-02 | 1.757934E-03 | 8.665805E-02 | -2.597243E-03 | 2.413315E-03 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller McQuay WDC 1973kW/6.28COP/Vanes CAPFT | 1.110884E+00 | 7.376077E-02 | -5.957719E-03 | -2.861037E-02 | -2.129104E-04 | 2.547028E-03 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller York YK 1997kW/7.24COP/Vanes CAPFT | 9.058272E-01 | 1.309175E-01 | -3.446620E-03 | -3.166792E-02 | 2.325200E-04 | -4.892256E-04 | 7.22 | 12.78 | 12.78 | 26.67
ElectricEIRChiller McQuay PFH 2043kW/8.44COP/Vanes CAPFT | 8.383569E-01 | 4.716323E-02 | -2.515385E-03 | -3.773603E-03 | -9.186324E-04 | 2.177057E-03 | 6.11 | 12.78 | 12.78 | 23.89
ElectricEIRChiller Trane CVHF 2043kW/9.08COP/Vanes CAPFT | -1.340241E+00 | 7.634284E-03 | -3.044184E-03 | 1.991327E-01 | -4.530240E-03 | 2.700765E-03 | 4.44 | 8.89 | 18.33 | 29.44
ElectricEIRChiller Carrier 19XL 2057kW/6.05COP/Vanes CAPFT | 7.737452E-01 | -1.249478E-02 | -3.193419E-03 | 2.110302E-02 | -1.188413E-03 | 3.820335E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YT 2110kW/7.15COP/Vanes CAPFT | 5.359238E-01 | 1.785857E-02 | 1.579272E-03 | 4.522868E-02 | -1.632172E-03 | 6.008061E-04 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller McQuay PFH 2124kW/6.03COP/Vanes CAPFT | 1.040134E+00 | -1.745650E-02 | 1.084856E-03 | 6.629328E-03 | -8.008991E-04 | 1.567769E-03 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YK 2159kW/6.85COP/Vanes CAPFT | 6.322235E-01 | 1.553954E-02 | -9.149770E-03 | 5.284289E-02 | -2.818835E-03 | 7.074096E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller Trane CVHF 2184kW/6.78COP/Vanes CAPFT | 1.235680E+00 | 2.213527E-02 | -1.770186E-03 | -1.131594E-02 | -5.008696E-04 | 1.356522E-03 | 5.56 | 10.00 | 18.33 | 23.89
ElectricEIRChiller York YK 2201kW/6.69COP/Vanes CAPFT | 5.474968E-01 | -4.800356E-03 | -6.845886E-03 | 6.302552E-02 | -2.911528E-03 | 6.598690E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller York YT 2233kW/9.54COP/VSD CAPFT | 7.139071E-01 | -4.174477E-02 | 5.188589E-03 | 4.350540E-02 | -1.632005E-03 | 9.364594E-04 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YT 2233kW/9.54COP/VSD CAPFT | 7.585741E-01 | -5.127829E-02 | 5.848602E-03 | 4.235544E-02 | -1.606561E-03 | 9.364594E-04 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YK 2237kW/6.41COP/Vanes CAPFT | 6.899710E-01 | -1.413334E-03 | -1.109323E-03 | 4.078120E-02 | -1.785625E-03 | 2.977821E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller York YK 2275kW/6.32COP/Vanes CAPFT | 7.655381E-01 | -1.570198E-02 | -3.331784E-04 | 3.610649E-02 | -1.642944E-03 | 3.016087E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller York YK 2275kW/6.32COP/Vanes CAPFT | 1.034673E+00 | -1.091064E-02 | 9.019479E-04 | 9.686229E-03 | -9.160783E-04 | 2.045641E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Trane CVHF 2300kW/8.10COP/Vanes CAPFT | 6.268137E-01 | 3.920902E-02 | -5.475881E-04 | 3.072669E-02 | -1.474615E-03 | 8.577783E-04 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Trane CVHF 2317kW/6.33COP/VSD CAPFT | 7.277716E-01 | 1.018101E-02 | -6.282438E-04 | 1.337701E-02 | -5.050352E-04 | 1.527259E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XR 2391kW/6.77COP/Vanes CAPFT | 3.676388E-01 | -5.087680E-02 | -1.772675E-03 | 9.518123E-02 | -3.403878E-03 | 4.526983E-03 | 6.67 | 12.22 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 2391kW/6.44COP/VSD CAPFT | 3.676388E-01 | -5.087680E-02 | -1.772675E-03 | 9.518123E-02 | -3.403878E-03 | 4.526983E-03 | 6.67 | 12.22 | 12.78 | 23.89
ElectricEIRChiller York YK 2412kW/5.58COP/Vanes CAPFT | 7.473817E-01 | 8.069214E-03 | 8.433986E-05 | 1.925706E-02 | -7.505775E-04 | 1.174526E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller McQuay PFH 2462kW/6.67COP/Vanes CAPFT | 9.561527E-01 | 5.742999E-02 | -4.868087E-03 | 1.799507E-02 | -1.793848E-03 | 3.194186E-03 | 5.56 | 8.89 | 12.78 | 23.89
ElectricEIRChiller Trane CVHF 2567kW/11.77COP/VSD CAPFT | 4.549428E-01 | 2.748161E-02 | -4.298342E-03 | 4.363928E-02 | -1.352509E-03 | 2.964225E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YK 2771kW/6.84COP/VSD CAPFT | 7.734286E-01 | 4.848829E-02 | -1.859209E-03 | 2.611971E-02 | -1.243562E-03 | 7.210181E-04 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller Trane CVHF 2799kW/6.40COP/Vanes CAPFT | 2.210324E-01 | -2.752320E-02 | 4.903763E-04 | 7.337449E-02 | -1.919426E-03 | 1.935659E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller York YT 3133kW/9.16COP/Vanes CAPFT | 7.607419E-01 | 1.323998E-02 | 6.902287E-04 | 1.510969E-02 | -9.443341E-04 | 1.484396E-03 | 5.56 | 8.89 | 12.78 | 29.44
ElectricEIRChiller McQuay PFH 3165kW/6.48COP/Vanes CAPFT | 1.342558E+00 | 7.520735E-02 | -8.988936E-03 | -3.340001E-02 | -6.065934E-04 | 4.684791E-03 | 5.56 | 8.89 | 12.78 | 23.89
ElectricEIRChiller McQuay PFH 4020kW/7.35COP/Vanes CAPFT | 8.958422E-01 | 3.762768E-02 | -3.550080E-03 | -4.322645E-03 | -1.194933E-03 | 3.006034E-03 | 6.67 | 12.22 | 12.78 | 23.89
ElectricEIRChiller York YK 4396kW/6.63COP/Vanes CAPFT | 3.693621E-01 | -7.284715E-02 | -4.871930E-03 | 1.223355E-01 | -5.368259E-03 | 1.035036E-02 | 4.44 | 7.78 | 12.78 | 26.67
ElectricEIRChiller York YK 4477kW/6.64COP/Vanes CAPFT | 4.844230E-01 | -9.879643E-02 | -2.516527E-03 | 1.144722E-01 | -5.101526E-03 | 1.022861E-02 | 4.44 | 7.78 | 12.78 | 26.67
ElectricEIRChiller York YK 4515kW/6.22COP/Vanes CAPFT | 3.732405E-01 | -7.176618E-03 | -2.588788E-03 | 5.381225E-02 | -1.773937E-03 | 3.509721E-03 | 4.44 | 7.78 | 12.78 | 26.67
ElectricEIRChiller York YK 4537kW/6.28COP/Vanes CAPFT | 9.418253E-01 | 8.142292E-02 | -9.532713E-03 | 3.185018E-02 | -2.583116E-03 | 5.294716E-03 | 4.44 | 7.78 | 12.78 | 26.67
ElectricEIRChiller Trane CVHF 4610kW/6.34COP/Vanes CAPFT | 8.614836E-01 | -3.988130E-03 | -1.643579E-03 | 8.882312E-03 | -3.930474E-04 | 1.593969E-03 | 4.44 | 8.89 | 18.33 | 29.44
ElectricEIRChiller Carrier 19EX 4667kW/6.16COP/Vanes CAPFT | 4.084496E-01 | -4.396326E-02 | -2.112120E-03 | 8.225310E-02 | -3.066058E-03 | 5.257550E-03 | 4.44 | 7.78 | 12.78 | 26.67
ElectricEIRChiller Trane CVHF 4677kW/6.27COP/Vanes CAPFT | 8.449416E-01 | -2.116553E-02 | 6.121458E-03 | 7.120879E-03 | -1.798959E-04 | -1.349219E-04 | 4.44 | 7.78 | 12.78 | 26.67
ElectricEIRChiller York YK 4966kW/6.05COP/Vanes CAPFT | 5.746486E-01 | -3.051134E-02 | -1.964984E-04 | 3.309783E-02 | -9.174714E-04 | 2.287276E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller York YK 4969kW/7.14COP/Vanes CAPFT | 7.817577E-01 | -1.012013E-01 | -1.584389E-03 | 7.928475E-02 | -3.674093E-03 | 7.999392E-03 | 4.44 | 8.89 | 12.78 | 29.44
ElectricEIRChiller York YK 4969kW/7.07COP/Vanes CAPFT | 1.803605E-01 | -9.685535E-02 | -5.831135E-03 | 1.341596E-01 | -5.279908E-03 | 1.045372E-02 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller Carrier 19EX 4997kW/6.40COP/Vanes CAPFT | 7.122762E-02 | 2.550937E-03 | -9.679482E-03 | 9.391204E-02 | -3.505261E-03 | 7.309943E-03 | 4.44 | 7.78 | 12.78 | 26.67
ElectricEIRChiller Carrier 19EX 5148kW/6.34COP/Vanes CAPFT | 3.564454E-01 | 2.020689E-02 | -6.286899E-03 | 5.760425E-02 | -2.102376E-03 | 4.126650E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller York YK 5170kW/7.15COP/Vanes CAPFT | 1.675697E-01 | -1.191228E-01 | -4.328384E-03 | 1.355905E-01 | -5.171251E-03 | 1.039840E-02 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller Carrier 19EX 5208kW/6.88COP/Vanes CAPFT | 5.563516E-01 | -4.106264E-02 | -3.164992E-03 | 5.722234E-02 | -2.313857E-03 | 5.377616E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller York YK 5465kW/6.94COP/Vanes CAPFT | 1.092441E-01 | -1.225892E-01 | -2.802873E-03 | 1.324138E-01 | -4.714937E-03 | 9.205744E-03 | 4.44 | 8.89 | 15.56 | 29.44
ElectricEIRChiller York YK 5549kW/6.50COP/Vanes CAPFT | -1.402079E-01 | 1.836029E-02 | -2.390588E-03 | 1.207956E-01 | -3.563147E-03 | 2.024532E-03 | 4.44 | 8.89 | 12.78 | 26.11
ElectricEIRChiller Carrier 19FA 5651kW/5.50COP/Vanes CAPFT | 1.299676E+00 | 1.790645E-02 | -2.522300E-03 | 2.536423E-03 | -1.128041E-03 | 3.003265E-03 | 4.44 | 8.89 | 15.56 | 29.44
DOE-2 Centrifugal/5.50COP CAPFT | 0.257896E+00 | 0.389016E-01 | -0.217080E-03 | 0.468684E-01 | -0.942840E-03 | -0.343440E-03 | 5.0 | 10.0 | 24.0 | 35.0
ElectricEIRChiller Multistack MS 172kW/3.67COP/None CAPFT | 9.839419E-01 | 1.094957E-01 | -4.547595E-03 | -2.311886E-02 | 2.595943E-04 | -5.093307E-04 | 4.44 | 8.89 | 18.33 | 35.00
DOE-2 Reciprocating/3.67COP CAPFT | 0.507883E+00 | 0.145228E+00 | -0.625644E-02 | -0.111780E-02 | -0.129600E-03 | -0.281880E-03 | 5.0 | 10.0 | 24.0 | 35.0
ElectricEIRChiller Trane RTWA 383kW/4.17COP/Valve CAPFT | 9.830684E-01 | 3.676199E-02 | 5.307995E-05 | -4.828624E-03 | -4.755963E-05 | -2.377982E-04 | 4.44 | 8.89 | 23.89 | 35.00
ElectricEIRChiller Trane RTHB 531kW/4.83COP/Valve CAPFT | 9.434012E-01 | 1.630729E-02 | 8.621098E-04 | 3.242384E-03 | -3.003973E-04 | 1.931126E-04 | 5.56 | 10.00 | 15.56 | 23.89
ElectricEIRChiller Trane RTHB 538kW/5.12COP/Valve CAPFT | 9.344780E-01 | 2.760000E-02 | 3.781512E-04 | -9.176470E-04 | -1.270588E-04 | -4.235294E-05 | 5.56 | 10.00 | 15.56 | 23.89
ElectricEIRChiller Trane RTHB 542kW/5.26COP/Valve CAPFT | 9.226438E-01 | 2.878831E-02 | 3.756957E-04 | -1.963636E-03 | -8.415584E-05 | -1.262338E-04 | 5.56 | 10.00 | 15.56 | 23.89
ElectricEIRChiller York YS 672kW/7.90COP/Valve CAPFT | 9.274375E-01 | 2.846559E-02 | 4.024428E-04 | -5.932730E-03 | -1.067418E-05 | -2.199015E-04 | 6.11 | 12.78 | 15.56 | 23.89
ElectricEIRChiller Carrier 23XL 686kW/5.91COP/Valve CAPFT | 2.903523E-01 | -2.676742E-02 | -4.771695E-03 | 8.162394E-02 | -3.028217E-03 | 5.712524E-03 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller Trane RTHC 707kW/7.77COP/Valve CAPFT | 9.362925E-01 | 2.940722E-02 | 5.726999E-04 | -5.696483E-03 | -5.569609E-05 | -1.708132E-04 | 5.56 | 11.11 | 15.56 | 23.89
ElectricEIRChiller York YS 756kW/7.41COP/Valve CAPFT | 9.432455E-01 | 2.794778E-02 | 2.937753E-04 | -5.818549E-03 | -3.764392E-05 | -5.777607E-05 | 5.56 | 10.00 | 16.06 | 23.89
ElectricEIRChiller York YS 781kW/5.42COP/Valve CAPFT | 1.002148E+00 | 3.300191E-02 | 3.741670E-04 | -5.925358E-03 | -2.599267E-05 | -2.172126E-04 | 4.44 | 8.89 | 15.56 | 35.00
ElectricEIRChiller Carrier 23XL 830kW/6.97COP/Valve CAPFT | 8.198506E-01 | 4.299516E-03 | -2.451574E-04 | 1.431034E-02 | -3.586302E-04 | 2.510412E-04 | 5.56 | 10.00 | 14.17 | 23.89
ElectricEIRChiller Carrier 23XL 862kW/6.11COP/Valve CAPFT | -3.646458E-02 | -6.061334E-02 | -3.708583E-03 | 1.197997E-01 | -3.723397E-03 | 5.368766E-03 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller Carrier 23XL 862kW/6.84COP/Valve CAPFT | -4.535842E-02 | -6.253871E-02 | -3.623064E-03 | 1.218299E-01 | -3.793440E-03 | 5.404739E-03 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller Carrier 23XL 865kW/6.05COP/Valve CAPFT | 5.079758E-01 | -2.344768E-02 | -3.296630E-03 | 3.508384E-02 | -8.359630E-04 | 2.585294E-03 | 3.33 | 7.78 | 12.78 | 29.44
ElectricEIRChiller York YS 879kW/5.82COP/Valve CAPFT | 1.031429E+00 | 3.364723E-02 | -2.735093E-04 | -3.789167E-03 | -1.553912E-04 | 2.782117E-04 | 3.33 | 7.78 | 12.78 | 29.44
ElectricEIRChiller Trane RTHC 1009kW/5.37COP/Valve CAPFT | 1.134633E+00 | 3.267210E-02 | 5.266344E-04 | -1.076173E-02 | -4.853769E-05 | -2.569325E-04 | 5.56 | 10.00 | 19.97 | 24.86
ElectricEIRChiller Trane RTHB 1051kW/5.05COP/Valve CAPFT | 9.482157E-01 | 3.306737E-02 | -6.450072E-05 | -3.756522E-03 | -6.501672E-05 | 2.517986E-15 | 4.44 | 8.89 | 23.89 | 35.00
ElectricEIRChiller Carrier 23XL 1062kW/5.50COP/Valve CAPFT | 1.025695E+00 | 2.327484E-02 | -4.693708E-03 | -7.092715E-03 | -3.754967E-04 | 2.843046E-03 | 6.67 | 10.00 | 21.11 | 29.44
ElectricEIRChiller Trane RTHC 1066kW/5.73COP/Valve CAPFT | 1.062396E+00 | 4.575299E-02 | 2.802795E-04 | -8.802343E-03 | -3.127891E-05 | -5.937227E-04 | 5.56 | 10.00 | 20.07 | 25.28
ElectricEIRChiller Trane RTHC 1094kW/6.55COP/Valve CAPFT | 9.643756E-01 | 3.820069E-02 | 4.611891E-04 | -5.174840E-03 | -5.784404E-05 | -2.944185E-04 | 5.56 | 10.00 | 15.56 | 23.89
ElectricEIRChiller Carrier 23XL 1108kW/6.92COP/Valve CAPFT | 6.631328E-01 | -1.027433E-02 | -5.388040E-04 | 3.320295E-02 | -1.304714E-03 | 2.169498E-03 | 5.56 | 10.00 | 12.78 | 23.89
ElectricEIRChiller York YS 1171kW/9.15COP/Valve CAPFT | 9.299045E-01 | 2.350383E-02 | -4.649409E-04 | -4.367237E-03 | -2.040112E-04 | 6.430038E-04 | 6.11 | 12.78 | 15.56 | 23.89
ElectricEIRChiller Carrier 23XL 1196kW/6.39COP/Valve CAPFT | 5.775948E-01 | 2.206074E-02 | -3.342365E-03 | 3.970188E-02 | -1.669877E-03 | 2.762827E-03 | 6.67 | 12.22 | 12.78 | 23.89
ElectricEIRChiller York YS 1554kW/9.31COP/Valve CAPFT | 1.083027E+00 | 9.278069E-03 | 1.175024E-03 | -1.395851E-02 | 9.301303E-05 | 6.968115E-05 | 5.56 | 8.89 | 15.56 | 35.00
ElectricEIRChiller York YS 1758kW/5.84COP/Valve CAPFT | 8.130185E-01 | -1.425368E-02 | -1.618007E-03 | 2.638417E-02 | -9.154379E-04 | 1.696015E-03 | 4.44 | 8.89 | 12.78 | 35.00
ElectricEIRChiller Trane CGWD 207kW/3.99COP/None CAPFT | 9.441897E-01 | 3.371079E-02 | 9.756685E-05 | -3.220573E-03 | -4.917369E-05 | -1.775717E-04 | 5.56 | 10.00 | 23.89 | 35.00

## CURVE BIQUADRATIC EIRFT
Name | Coeff1 Constant | Coeff2 x | Coeff3 x**2 | Coeff4 y | Coeff5 y**2 | Coeff6 x*y | minimum value of x | maximum value of x | minimum value of y | maximum value of y | minimum value of y | maximum value of y
Curve名称 | 常数项C1 | x系数C2 | X2系数C3 | y系数C4 | y2系数C5 | xy系数C6 | x的最小值 | x的最大值 | y的最小值 | y的最大值 | y的最小值 | y的最大值
系数
ElectricEIRChiller McQuay WSC 471kW/5.89COP/Vanes EIRFT | 4.475238E-01 | -2.588210E-02 | -1.459053E-03 | 4.342595E-02 | -1.000651E-03 | 1.920106E-03 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller York YT 563kW/10.61COP/Vanes EIRFT | -5.781003E-01 | -1.169130E-01 | -4.760535E-03 | 2.230082E-01 | -5.313649E-03 | 6.846644E-03 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller McQuay PEH 703kW/7.03COP/Vanes EIRFT | 8.234029E-01 | -1.171542E-01 | 5.869351E-04 | 2.964642E-02 | -9.190377E-04 | 5.035796E-03 | 5.56 | 8.89 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 23XL 724kW/6.04COP/Vanes EIRFT | 5.059102E-01 | -1.621557E-02 | 3.346388E-04 | 2.350906E-02 | 3.514201E-04 | -6.342981E-04 | 5.56 | 10.00 | 13.75 | 23.89 | 13.75 | 23.89
ElectricEIRChiller Carrier 19XR 742kW/5.42COP/VSD EIRFT | 9.946139E-01 | -4.829399E-02 | 4.674277E-04 | -1.158726E-03 | 5.762583E-04 | 2.148192E-04 | 5.56 | 10.00 | 11.25 | 23.89 | 11.25 | 23.89
ElectricEIRChiller McQuay WSC 816kW/6.74COP/Vanes EIRFT | 7.335321E-01 | 4.465107E-04 | -3.448575E-03 | 3.770822E-03 | -2.189675E-04 | 2.400267E-03 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller McQuay PEH 819kW/8.11COP/Vanes EIRFT | 5.925176E-01 | -1.908391E-02 | -1.852692E-03 | 4.051551E-02 | -2.908719E-04 | 1.059047E-03 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XR 823kW/6.28COP/Vanes EIRFT | 8.029134E-01 | 2.171359E-02 | 2.388123E-04 | -1.096173E-02 | 1.065277E-03 | -2.057538E-03 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 869kW/5.57COP/VSD EIRFT | 3.943721E-01 | 1.079147E-01 | -8.912223E-03 | -3.229487E-04 | 1.302402E-05 | 1.561862E-03 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 897kW/7.23COP/VSD EIRFT | 6.511011E-01 | 4.948557E-02 | -8.152733E-04 | 2.322946E-02 | 1.990802E-04 | -2.669401E-03 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 897kW/6.50COP/Vanes EIRFT | 8.527749E-01 | -4.336881E-03 | 8.972177E-04 | -1.888039E-03 | 8.648075E-04 | -1.438797E-03 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YT 897kW/7.60COP/VSD EIRFT | 5.526128E-01 | 3.299472E-03 | -7.981925E-04 | 4.245710E-02 | -3.533658E-04 | -9.415137E-04 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YT 897kW/6.27COP/VSD EIRFT | 5.530767E-01 | -5.683068E-02 | 4.423475E-03 | 6.472411E-02 | -7.378933E-04 | -2.491202E-03 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 897kW/6.23COP/VSD EIRFT | 8.606461E-01 | -1.202294E-03 | 9.398625E-04 | 2.983262E-03 | 4.119228E-04 | -1.123884E-03 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller McQuay PFH 932kW/5.09COP/Vanes EIRFT | 6.053491E-01 | -1.089778E-02 | -1.511327E-03 | 1.902687E-02 | -1.910750E-04 | 9.008184E-04 | 3.33 | 7.78 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YT 960kW/4.64COP/Vanes EIRFT | 5.735924E-01 | 2.270414E-02 | -3.331832E-03 | 6.025574E-03 | 3.245033E-04 | 3.229690E-05 | 3.33 | 7.78 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YT 1023kW/5.81COP/Vanes EIRFT | 5.254964E-01 | -1.972389E-02 | 3.441072E-04 | 1.651466E-02 | 2.005198E-04 | -3.193246E-04 | 4.44 | 8.89 | 12.78 | 35.00 | 12.78 | 35.00
ElectricEIRChiller McQuay PEH 1030kW/8.58COP/Vanes EIRFT | 7.125878E-01 | 1.388940E-02 | -2.473407E-03 | 2.096719E-02 | -1.566098E-04 | 6.035460E-04 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YT 1048kW/6.06COP/Vanes EIRFT | 7.255594E-01 | -3.502968E-02 | 2.213476E-03 | 3.925410E-03 | 5.538176E-04 | -8.638012E-04 | 4.44 | 8.89 | 15.56 | 35.00 | 15.56 | 35.00
ElectricEIRChiller York YT 1055kW/5.96COP/Vanes EIRFT | 5.245110E-01 | -2.850126E-02 | 8.034720E-04 | 1.893133E-02 | 1.151629E-04 | -9.340642E-05 | 4.44 | 8.89 | 12.78 | 35.00 | 12.78 | 35.00
ElectricEIRChiller Carrier 19XR 1076kW/5.52COP/Vanes EIRFT | 7.511044E-01 | 2.415573E-02 | -5.310959E-03 | -1.073812E-03 | 1.189538E-04 | 1.604476E-03 | 5.56 | 10.00 | 12.78 | 24.89 | 12.78 | 24.89
ElectricEIRChiller Trane CVHE 1080kW/7.39COP/Vanes EIRFT | 3.608716E-01 | -5.637178E-02 | -3.428415E-04 | 4.230087E-02 | -4.391632E-04 | 1.517182E-03 | 5.56 | 10.00 | 16.24 | 23.61 | 16.24 | 23.61
ElectricEIRChiller York YT 1090kW/7.57COP/VSD EIRFT | 9.241019E-01 | -4.961574E-02 | 1.291675E-04 | 3.299013E-02 | -6.769477E-04 | 1.692815E-03 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller McQuay PEH 1104kW/8.00COP/Vanes EIRFT | 8.655242E-01 | -3.808337E-04 | -1.320050E-03 | 1.137834E-02 | -4.095120E-05 | 6.531102E-04 | 6.67 | 12.22 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YT 1125kW/7.92COP/VSD EIRFT | 6.542286E-01 | -2.451604E-02 | 1.253508E-03 | 4.216477E-02 | 1.404867E-04 | -1.508780E-03 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Trane CVHE 1125kW/4.89COP/Vanes EIRFT | 5.810580E-01 | -4.344257E-02 | -5.369108E-04 | 2.844405E-02 | -1.609390E-04 | 7.004346E-04 | 5.56 | 10.00 | 15.56 | 23.89 | 15.56 | 23.89
ElectricEIRChiller York YT 1125kW/7.92COP/VSD EIRFT | 6.542286E-01 | -2.451604E-02 | 1.253508E-03 | 4.216477E-02 | 1.404867E-04 | -1.508780E-03 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Trane CVHE 1129kW/7.19COP/Vanes EIRFT | 3.742142E-01 | -5.536709E-02 | -8.199663E-04 | 4.655032E-02 | -7.312591E-04 | 1.887184E-03 | 5.56 | 10.00 | 15.56 | 23.89 | 15.56 | 23.89
ElectricEIRChiller Carrier 19XR 1143kW/6.57COP/VSD EIRFT | 9.475580E-01 | -1.187942E-02 | 8.799326E-05 | 2.250775E-04 | 1.815775E-04 | 2.178409E-04 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 1157kW/5.62COP/VSD EIRFT | 1.075567E+00 | -3.893571E-02 | 1.082499E-03 | -5.782829E-03 | 6.574492E-04 | -5.302886E-04 | 5.56 | 10.00 | 11.25 | 23.89 | 11.25 | 23.89
ElectricEIRChiller Carrier 19XR 1196kW/6.50COP/Vanes EIRFT | 9.514432E-01 | -2.252147E-02 | -1.062456E-05 | -1.383194E-04 | 3.914644E-04 | 8.126485E-05 | 6.67 | 12.22 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1213kW/7.78COP/Vanes EIRFT | 1.002142E+00 | -2.505239E-02 | 5.169707E-04 | 6.321862E-03 | 5.116807E-04 | -4.794244E-04 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller McQuay PEH 1231kW/6.18COP/Vanes EIRFT | 8.067591E-01 | 1.868314E-02 | -5.569088E-03 | -4.309148E-03 | 1.373034E-04 | 2.394081E-03 | 5.56 | 8.89 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1234kW/5.39COP/VSD EIRFT | 3.771659E-01 | 1.144965E-01 | -8.186893E-03 | -3.372584E-03 | 1.689440E-04 | 1.008523E-03 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 1259kW/6.26COP/Vanes EIRFT | 7.582035E-01 | 6.896017E-03 | -1.491911E-03 | 2.249459E-03 | 3.908697E-04 | -1.735265E-04 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller York YK 1259kW/6.45COP/Vanes EIRFT | 8.991536E-01 | 6.305932E-03 | -3.756374E-04 | -1.952076E-02 | 1.381302E-03 | -1.615004E-03 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller York YT 1266kW/4.39COP/Vanes EIRFT | 8.284925E-02 | 4.206167E-02 | -5.254555E-03 | 1.964407E-02 | 1.070646E-04 | 2.298241E-04 | 5.56 | 8.89 | 12.78 | 35.00 | 12.78 | 35.00
ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes EIRFT | 7.815645E-01 | -2.448971E-02 | 1.644370E-03 | 5.564580E-03 | 5.800428E-04 | -1.086993E-03 | 5.56 | 8.89 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes EIRFT | 7.815645E-01 | -2.448971E-02 | 1.644370E-03 | 5.564580E-03 | 5.800428E-04 | -1.086993E-03 | 5.56 | 8.89 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1294kW/7.61COP/Vanes EIRFT | 1.085249E+00 | -9.441252E-04 | -2.505100E-03 | -8.724367E-03 | 4.164780E-04 | 8.473746E-04 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Trane CVHE 1329kW/5.38COP/Vanes EIRFT | 8.074052E-01 | 3.355495E-02 | -1.549617E-03 | -7.142554E-03 | 5.056363E-04 | -7.547786E-04 | 6.11 | 10.00 | 21.11 | 29.44 | 21.11 | 29.44
ElectricEIRChiller Carrier 19XR 1350kW/7.90COP/VSD EIRFT | 9.953536E-01 | -3.118863E-02 | 2.094171E-03 | 7.086716E-03 | 7.387078E-04 | -1.384330E-03 | 5.56 | 8.89 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YT 1368kW/7.35COP/VSD EIRFT | 3.227543E-01 | -1.415418E-02 | -5.090650E-03 | 4.606511E-02 | -8.769578E-04 | 2.600343E-03 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Trane CVHE 1372kW/7.49COP/Vanes EIRFT | 9.123765E-01 | 1.616509E-02 | 1.906349E-03 | -1.143164E-02 | 1.080775E-03 | -2.873661E-03 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YT 1396kW/7.35COP/Vanes EIRFT | 5.207500E-01 | -9.073869E-03 | -1.812171E-04 | 2.568740E-02 | 4.255936E-05 | -5.899242E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XR 1403kW/7.09COP/VSD EIRFT | 1.098641E+00 | -2.485880E-02 | -6.240421E-05 | -1.719488E-03 | 4.887321E-04 | 9.618075E-05 | 6.67 | 12.22 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YT 1403kW/6.94COP/VSD EIRFT | 3.983846E-01 | 2.396665E-02 | -6.601871E-03 | 2.944077E-02 | -4.570885E-04 | 1.873209E-03 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Trane CVHE 1407kW/7.14COP/VSD EIRFT | 5.674858E-01 | 4.461513E-02 | -6.341978E-03 | 4.674972E-03 | 4.387295E-04 | 2.778096E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller McQuay PFH 1407kW/6.60COP/Vanes EIRFT | 7.929709E-01 | 3.424884E-02 | -5.567434E-03 | -6.974667E-03 | 2.531138E-04 | 1.862577E-03 | 5.56 | 8.89 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1407kW/6.04COP/VSD EIRFT | 1.026340E+00 | -1.612819E-02 | -1.092591E-03 | -1.784393E-02 | 7.961842E-04 | -9.586049E-05 | 4.44 | 10.00 | 12.78 | 32.22 | 12.78 | 32.22
ElectricEIRChiller Carrier 19XR 1410kW/8.54COP/VSD EIRFT | 1.131014E+00 | -6.735406E-02 | 3.034309E-06 | 1.307361E-02 | 3.384625E-04 | 7.872113E-04 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Trane CVHE 1442kW/6.61COP/VSD EIRFT | 6.287646E-01 | -3.024605E-02 | 6.137016E-04 | 1.805826E-02 | 1.640653E-04 | -1.113802E-04 | 4.44 | 8.89 | 12.78 | 35.00 | 12.78 | 35.00
ElectricEIRChiller York YT 1459kW/6.40COP/VSD EIRFT | 1.438935E-01 | 9.821191E-02 | -1.174270E-02 | 3.748666E-02 | -5.700518E-04 | 1.053698E-03 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Trane CVHE 1484kW/9.96COP/VSD EIRFT | -3.693940E-01 | -6.387787E-02 | -2.760494E-04 | 1.661135E-01 | -3.105485E-03 | 1.705909E-03 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YT 1495kW/7.51COP/VSD EIRFT | 7.106985E-01 | -2.087623E-01 | 9.421379E-03 | 8.491925E-02 | -1.260820E-03 | 1.125512E-03 | 5.56 | 8.89 | 12.78 | 35.00 | 12.78 | 35.00
ElectricEIRChiller McQuay WSC 1519kW/7.10COP/Vanes EIRFT | 9.981236E-01 | -1.060763E-02 | -3.921458E-03 | -1.206761E-02 | -1.398595E-04 | 3.467199E-03 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 1558kW/5.81COP/VSD EIRFT | 1.099343E+00 | -3.132676E-02 | 4.108521E-04 | -7.377845E-03 | 5.775048E-04 | -3.528472E-04 | 5.56 | 10.00 | 11.94 | 23.89 | 11.94 | 23.89
ElectricEIRChiller Carrier 19XR 1586kW/5.53COP/VSD EIRFT | 1.110611E+00 | -3.795765E-02 | 2.851444E-04 | -4.560404E-03 | 4.044229E-04 | 1.407332E-04 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller McQuay PEH 1635kW/7.47COP/Vanes EIRFT | 1.040733E+00 | -7.118888E-02 | 2.262395E-03 | 1.221901E-02 | 2.152693E-04 | 7.409943E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XR 1635kW/6.36COP/Vanes EIRFT | 7.355981E-01 | -1.083354E-02 | -9.244662E-04 | 1.458943E-02 | 8.494647E-06 | 1.279572E-04 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller Carrier 19XR 1656kW/8.24COP/VSD EIRFT | 7.730916E-01 | -8.073559E-02 | -2.161313E-03 | 6.144398E-02 | -1.953734E-03 | 4.056527E-03 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YT 1663kW/9.34COP/Vanes EIRFT | 1.028094E+00 | -6.127553E-02 | 3.236371E-03 | 1.656482E-02 | 2.976850E-04 | -4.418361E-04 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XL 1674kW/7.89COP/Vanes EIRFT | 9.868510E-01 | -6.325526E-02 | 3.498632E-03 | 1.699731E-02 | 2.573490E-04 | -4.233553E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Trane CVHF 1681kW/6.59COP/Vanes EIRFT | 4.344630E-01 | -5.781149E-03 | 2.852311E-04 | 2.723246E-02 | 1.280801E-04 | -8.964328E-04 | 5.56 | 10.00 | 18.33 | 23.89 | 18.33 | 23.89
ElectricEIRChiller Carrier 19XR 1723kW/8.32COP/VSD EIRFT | 2.950574E-01 | -1.036684E-01 | -4.169567E-03 | 1.256790E-01 | -4.004203E-03 | 6.718687E-03 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 1727kW/9.04COP/Vanes EIRFT | 1.072553E+00 | -8.058631E-03 | -2.109608E-03 | -1.262910E-03 | 6.155442E-04 | 4.796754E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller McQuay WSC 1751kW/6.73COP/Vanes EIRFT | 8.089395E-01 | 2.628482E-02 | -1.773497E-03 | -8.118430E-03 | 7.146809E-04 | -6.481705E-04 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller Trane CVHF 1758kW/5.96COP/Vanes EIRFT | 4.910329E-01 | -9.895115E-02 | 4.257871E-03 | 5.433817E-02 | -8.184909E-04 | 6.178810E-04 | 5.56 | 10.00 | 12.78 | 24.44 | 12.78 | 24.44
ElectricEIRChiller York YT 1758kW/5.76COP/VSD EIRFT | 6.794525E-01 | 6.694756E-02 | -3.625396E-03 | -1.018762E-02 | 1.066394E-03 | -2.113402E-03 | 5.56 | 10.51 | 12.78 | 24.44 | 12.78 | 24.44
ElectricEIRChiller York YT 1758kW/6.26COP/Vanes EIRFT | 2.311197E-01 | 9.581517E-02 | -5.672726E-03 | 2.766035E-02 | -1.411214E-04 | -1.011216E-03 | 5.56 | 10.00 | 12.78 | 24.44 | 12.78 | 24.44
ElectricEIRChiller York YT 1758kW/5.96COP/Vanes EIRFT | 4.949320E-01 | 9.099785E-03 | -6.935841E-04 | 3.277452E-02 | -3.895481E-04 | -5.524011E-04 | 5.56 | 10.00 | 12.78 | 24.44 | 12.78 | 24.44
ElectricEIRChiller Trane CVHE 1758kW/5.96COP/Vanes EIRFT | 1.243313E+00 | -3.031784E-02 | 3.452464E-03 | -2.739941E-02 | 9.141695E-04 | -1.000080E-03 | 4.44 | 8.89 | 23.89 | 35.00 | 23.89 | 35.00
ElectricEIRChiller York YT 1758kW/6.28COP/Vanes EIRFT | 5.605391E-01 | -1.377994E-02 | 6.569542E-05 | 1.321951E-02 | 2.686074E-04 | -5.011451E-04 | 4.44 | 8.89 | 15.56 | 35.00 | 15.56 | 35.00
ElectricEIRChiller Carrier 19XR 1758kW/5.86COP/VSD EIRFT | 1.743365E-01 | -5.054806E-02 | -5.424748E-03 | 8.244673E-02 | -2.400392E-03 | 5.078720E-03 | 5.56 | 10.00 | 12.78 | 24.44 | 12.78 | 24.44
ElectricEIRChiller Trane CVHF 1758kW/6.46COP/VSD EIRFT | 7.989434E-02 | 2.062907E-02 | -4.050827E-04 | 4.570552E-02 | -1.469163E-04 | -1.563259E-03 | 5.56 | 10.00 | 12.78 | 24.44 | 12.78 | 24.44
ElectricEIRChiller Trane CVHF 1758kW/6.87COP/Vanes EIRFT | 6.329473E-01 | 5.521802E-03 | 1.487172E-04 | 2.433576E-03 | 7.100129E-04 | -1.108627E-03 | 5.56 | 10.00 | 12.78 | 24.44 | 12.78 | 24.44
ElectricEIRChiller Carrier 19XR 1776kW/8.00COP/Vanes EIRFT | 8.006719E-01 | -3.137026E-02 | 4.098888E-04 | 3.176921E-02 | -2.104567E-04 | -7.660277E-05 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XL 1779kW/6.18COP/Vanes EIRFT | 5.872331E-01 | -3.907248E-02 | 3.474913E-04 | 2.950392E-02 | -2.510016E-04 | 2.481610E-04 | 4.44 | 8.89 | 15.56 | 26.11 | 15.56 | 26.11
ElectricEIRChiller Trane CVHF 1779kW/6.18COP/Vanes EIRFT | 3.137523E-01 | -1.879556E-02 | -1.860907E-03 | 3.469711E-02 | -1.503480E-04 | 7.641242E-04 | 5.56 | 10.00 | 18.33 | 23.89 | 18.33 | 23.89
ElectricEIRChiller York YT 1794kW/8.11COP/Vanes EIRFT | 8.546274E-01 | 2.456473E-01 | -9.770595E-03 | -7.386557E-02 | 2.843499E-03 | -5.292981E-03 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YT 1794kW/7.90COP/VSD EIRFT | 5.984829E-01 | -1.552700E-01 | 6.909012E-03 | 6.801572E-02 | -7.450754E-04 | 5.764600E-04 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XL 1797kW/5.69COP/Vanes EIRFT | 1.084290E+00 | -4.318103E-02 | 1.586113E-03 | 1.664015E-03 | 8.043383E-05 | 5.681056E-05 | 6.67 | 10.00 | 21.11 | 29.44 | 21.11 | 29.44
ElectricEIRChiller Carrier 19XR 1801kW/6.34COP/VSD EIRFT | 6.931082E-01 | -1.885558E-02 | 8.345461E-04 | 1.263879E-02 | 4.588028E-04 | -8.221467E-04 | 6.67 | 12.22 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YT 1867kW/10.09COP/Vanes EIRFT | 6.668391E-01 | 1.506485E-02 | -4.249134E-03 | 3.588996E-02 | -1.681591E-04 | 7.028459E-04 | 4.44 | 8.89 | 12.78 | 35.00 | 12.78 | 35.00
ElectricEIRChiller Carrier 19XL 1871kW/6.49COP/Vanes EIRFT | 1.029608E+00 | -7.149045E-02 | 2.043279E-03 | -6.116474E-04 | 3.908334E-04 | 6.870233E-04 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller York YT 1881kW/6.77COP/VSD EIRFT | 6.175311E-01 | -3.913241E-02 | 6.177961E-04 | 2.775640E-02 | -2.151466E-04 | 5.514895E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YK 1881kW/6.53COP/Vanes EIRFT | 4.434989E-01 | 4.361264E-02 | -1.733337E-03 | 9.915503E-03 | 4.312717E-04 | -1.122346E-03 | 7.22 | 12.78 | 9.44 | 26.67 | 9.44 | 26.67
ElectricEIRChiller York YK 1881kW/6.53COP/Vanes EIRFT | 4.434989E-01 | 4.361264E-02 | -1.733337E-03 | 9.915503E-03 | 4.312717E-04 | -1.122346E-03 | 7.22 | 12.78 | 9.44 | 26.67 | 9.44 | 26.67
ElectricEIRChiller McQuay PEH 1895kW/6.42COP/Vanes EIRFT | 3.915073E-01 | -4.399727E-02 | -3.868294E-06 | 4.623771E-02 | -7.092319E-04 | 1.372133E-03 | 4.44 | 8.89 | 12.78 | 35.00 | 12.78 | 35.00
ElectricEIRChiller York YT 1934kW/7.55COP/Vanes EIRFT | 1.173674E+00 | -1.301647E-01 | 5.588446E-03 | 8.605153E-03 | 7.234201E-05 | 1.314581E-03 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller McQuay PEH 1934kW/6.01COP/Vanes EIRFT | 2.885371E-01 | -5.877829E-03 | -1.807763E-03 | 5.193076E-02 | -7.936373E-04 | 1.108590E-03 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller McQuay WDC 1973kW/6.28COP/Vanes EIRFT | 1.097378E+00 | -3.018324E-02 | -2.792200E-03 | -1.252428E-02 | 2.095232E-04 | 2.409252E-03 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller York YK 1997kW/7.24COP/Vanes EIRFT | 1.188194E-01 | 8.769791E-02 | -1.692086E-03 | 2.209962E-03 | 1.327958E-03 | -3.249833E-03 | 7.22 | 12.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller McQuay PFH 2043kW/8.44COP/Vanes EIRFT | 7.891693E-01 | 1.168677E-02 | -1.825470E-03 | 1.278749E-02 | 1.521317E-04 | 2.156746E-04 | 6.11 | 12.78 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Trane CVHF 2043kW/9.08COP/Vanes EIRFT | 6.065177E-01 | 1.178669E-02 | 2.098586E-03 | 1.532536E-02 | 6.756887E-04 | -2.629852E-03 | 4.44 | 8.89 | 18.33 | 29.44 | 18.33 | 29.44
ElectricEIRChiller Carrier 19XL 2057kW/6.05COP/Vanes EIRFT | 8.623086E-01 | -5.844490E-02 | -2.284745E-03 | 2.469188E-02 | -1.022604E-03 | 3.996523E-03 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YT 2110kW/7.15COP/Vanes EIRFT | 6.270855E-01 | -4.119654E-02 | 1.327107E-03 | 2.661446E-02 | -1.856827E-04 | 5.094942E-04 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller McQuay PFH 2124kW/6.03COP/Vanes EIRFT | 1.157799E+00 | -3.621524E-02 | -3.684818E-03 | -1.202959E-02 | -7.378548E-05 | 3.787365E-03 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YK 2159kW/6.85COP/Vanes EIRFT | 9.106730E-01 | -3.786410E-03 | -1.084261E-03 | -7.148246E-03 | 5.178799E-04 | 1.818623E-05 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller Trane CVHF 2184kW/6.78COP/Vanes EIRFT | 8.877947E-01 | -1.334886E-02 | 1.689581E-03 | -1.599710E-03 | 7.884945E-04 | -1.584900E-03 | 5.56 | 10.00 | 18.33 | 23.89 | 18.33 | 23.89
ElectricEIRChiller York YK 2201kW/6.69COP/Vanes EIRFT | 8.234137E-01 | 1.308264E-02 | -1.147806E-03 | -4.071161E-03 | 5.220869E-04 | -6.312495E-04 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller York YT 2233kW/9.54COP/VSD EIRFT | 7.145541E-01 | -1.074745E-02 | -1.010204E-03 | 3.081188E-02 | 1.061200E-04 | -4.325357E-04 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YT 2233kW/9.54COP/VSD EIRFT | 7.563409E-01 | -1.966623E-02 | -3.927494E-04 | 2.973607E-02 | 1.299230E-04 | -4.325357E-04 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YK 2237kW/6.41COP/Vanes EIRFT | 8.567950E-01 | 3.354557E-03 | 1.047901E-03 | -5.217250E-03 | 6.565310E-04 | -1.361740E-03 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller York YK 2275kW/6.32COP/Vanes EIRFT | 8.164026E-01 | 1.682749E-02 | 6.236204E-05 | -6.058245E-03 | 7.008780E-04 | -1.422110E-03 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller York YK 2275kW/6.32COP/Vanes EIRFT | 8.326094E-01 | -6.056615E-03 | -3.016626E-04 | -2.498578E-03 | 4.933363E-04 | -3.125632E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Trane CVHF 2300kW/8.10COP/Vanes EIRFT | 7.178121E-01 | 6.561784E-03 | 8.193740E-06 | 2.319141E-02 | -1.755983E-06 | -8.834410E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Trane CVHF 2317kW/6.33COP/VSD EIRFT | 3.502330E-01 | -2.301510E-02 | 5.749596E-04 | 1.902421E-02 | 3.109974E-04 | -4.714517E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Carrier 19XR 2391kW/6.77COP/Vanes EIRFT | 6.266646E-01 | -2.367443E-02 | 4.031296E-04 | 2.827714E-02 | -1.985242E-04 | -1.470260E-04 | 6.67 | 12.22 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 19XR 2391kW/6.44COP/VSD EIRFT | 6.230142E-01 | -2.371649E-02 | 3.996265E-04 | 2.874515E-02 | -2.115103E-04 | -1.526191E-04 | 6.67 | 12.22 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YK 2412kW/5.58COP/Vanes EIRFT | 4.626807E-01 | -2.305674E-02 | 1.169126E-03 | 3.431185E-02 | -3.396938E-04 | -7.381352E-05 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller McQuay PFH 2462kW/6.67COP/Vanes EIRFT | 5.462893E-01 | 2.854651E-02 | -5.770782E-03 | 1.634571E-02 | -2.645314E-04 | 2.138325E-03 | 5.56 | 8.89 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Trane CVHF 2567kW/11.77COP/VSD EIRFT | 4.561990E-01 | -3.333063E-02 | -1.763576E-03 | 5.624520E-02 | -8.535085E-05 | 3.567604E-04 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YK 2771kW/6.84COP/VSD EIRFT | 7.203736E-01 | 1.030460E-02 | -7.854237E-04 | -1.206349E-03 | 8.210060E-04 | -1.455414E-03 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Trane CVHF 2799kW/6.40COP/Vanes EIRFT | 2.267558E-01 | -7.615857E-02 | 2.140583E-03 | 7.088812E-02 | -1.124968E-03 | 6.089843E-04 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller York YT 3133kW/9.16COP/Vanes EIRFT | 9.150153E-01 | -3.956395E-02 | 1.865473E-03 | 1.810633E-02 | 2.900613E-04 | -4.199110E-04 | 5.56 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller McQuay PFH 3165kW/6.48COP/Vanes EIRFT | 9.347904E-01 | 6.551597E-02 | -1.242676E-02 | -2.799974E-02 | 3.323287E-04 | 4.803491E-03 | 5.56 | 8.89 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller McQuay PFH 4020kW/7.35COP/Vanes EIRFT | 9.322623E-01 | -2.157964E-02 | -1.435883E-03 | 1.379036E-02 | -1.491048E-04 | 1.302075E-03 | 6.67 | 12.22 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YK 4396kW/6.63COP/Vanes EIRFT | 5.913358E-01 | -5.974145E-02 | 8.176561E-04 | 3.987353E-02 | -8.176694E-04 | 1.457994E-03 | 4.44 | 7.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller York YK 4477kW/6.64COP/Vanes EIRFT | 4.264570E-01 | -3.391606E-02 | -1.991396E-03 | 5.032090E-02 | -1.140771E-03 | 1.814692E-03 | 4.44 | 7.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller York YK 4515kW/6.22COP/Vanes EIRFT | 5.908290E-01 | 1.028668E-02 | -4.718838E-04 | 1.220347E-02 | 4.166971E-04 | -1.484327E-03 | 4.44 | 7.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller York YK 4537kW/6.28COP/Vanes EIRFT | 7.709829E-01 | -2.257680E-02 | 2.492708E-04 | 7.635418E-03 | 3.376522E-04 | -3.614203E-04 | 4.44 | 7.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller Trane CVHF 4610kW/6.34COP/Vanes EIRFT | 7.415078E-01 | -4.779029E-02 | -1.028085E-03 | 1.423650E-02 | 1.304315E-04 | 9.170177E-04 | 4.44 | 8.89 | 18.33 | 29.44 | 18.33 | 29.44
ElectricEIRChiller Carrier 19EX 4667kW/6.16COP/Vanes EIRFT | 5.214788E-01 | -8.218594E-03 | -3.068358E-05 | 2.152332E-02 | 1.203908E-04 | -7.167755E-04 | 4.44 | 7.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller Trane CVHF 4677kW/6.27COP/Vanes EIRFT | 8.283132E-01 | -3.030491E-02 | 4.164965E-03 | -3.278448E-03 | 6.762508E-04 | -1.107762E-03 | 4.44 | 7.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller York YK 4966kW/6.05COP/Vanes EIRFT | 8.229769E-01 | -8.128614E-03 | 1.110212E-03 | -3.521351E-03 | 6.129803E-04 | -9.170063E-04 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller York YK 4969kW/7.14COP/Vanes EIRFT | 7.382162E-01 | -5.847442E-02 | 1.117191E-03 | 2.168089E-02 | -2.189722E-04 | 1.036877E-03 | 4.44 | 8.89 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YK 4969kW/7.07COP/Vanes EIRFT | 7.220087E-01 | -4.480691E-02 | 9.621038E-06 | 2.084835E-02 | -2.615973E-04 | 1.188407E-03 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller Carrier 19EX 4997kW/6.40COP/Vanes EIRFT | 6.685097E-01 | -2.541433E-02 | 3.334144E-03 | 1.002578E-02 | 5.753780E-04 | -1.801340E-03 | 4.44 | 7.78 | 12.78 | 26.67 | 12.78 | 26.67
ElectricEIRChiller Carrier 19EX 5148kW/6.34COP/Vanes EIRFT | 5.426449E-01 | 3.961314E-03 | -1.195821E-04 | 1.609421E-02 | 3.089258E-04 | -1.129525E-03 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller York YK 5170kW/7.15COP/Vanes EIRFT | 5.894383E-01 | -2.926530E-02 | -1.900238E-03 | 2.849479E-02 | -5.105015E-04 | 1.702334E-03 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller Carrier 19EX 5208kW/6.88COP/Vanes EIRFT | 5.198204E-01 | -1.523340E-02 | -6.391523E-04 | 2.170049E-02 | 2.423693E-05 | 1.432604E-04 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller York YK 5465kW/6.94COP/Vanes EIRFT | 6.396022E-01 | -5.954060E-02 | 5.884523E-04 | 3.170651E-02 | -5.088216E-04 | 1.460759E-03 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
ElectricEIRChiller York YK 5549kW/6.50COP/Vanes EIRFT | 4.989980E-01 | -8.246157E-02 | 6.047523E-03 | 5.168793E-02 | -8.552445E-04 | 6.275326E-05 | 4.44 | 8.89 | 12.78 | 26.11 | 12.78 | 26.11
ElectricEIRChiller Carrier 19FA 5651kW/5.50COP/Vanes EIRFT | 7.853207E-01 | -1.652255E-02 | -3.294526E-04 | 4.569179E-03 | 1.964013E-04 | 1.761497E-04 | 4.44 | 8.89 | 15.56 | 29.44 | 15.56 | 29.44
DOE-2 Centrifugal/5.50COP EIRFT | 0.933884E+00 | -0.582120E-01 | 0.450036E-02 | 0.243000E-02 | 0.486000E-03 | -0.121500E-02 | 5.0 | 10.0 | 24.0 | 35.0 | 24.0 | 35.0
ElectricEIRChiller Multistack MS 172kW/3.67COP/None EIRFT | 9.396181E-01 | -5.754225E-02 | 2.561677E-03 | 1.081450E-02 | 1.839935E-04 | 5.269319E-05 | 4.44 | 8.89 | 18.33 | 35.00 | 18.33 | 35.00
DOE-2 Reciprocating/3.67COP EIRFT | 0.103076E+01 | -0.103536E+00 | 0.710208E-02 | 0.931860E-02 | 0.317520E-03 | -0.104328E-02 | 5.0 | 10.0 | 24.0 | 35.0 | 24.0 | 35.0
ElectricEIRChiller Trane RTWA 383kW/4.17COP/Valve EIRFT | 6.228513E-01 | -8.700783E-03 | 9.719796E-04 | 5.184584E-03 | 4.951699E-04 | -9.632370E-04 | 4.44 | 8.89 | 23.89 | 35.00 | 23.89 | 35.00
ElectricEIRChiller Trane RTHB 531kW/4.83COP/Valve EIRFT | 4.524778E-01 | 1.045156E-04 | 6.932509E-05 | 2.044980E-02 | 3.672953E-04 | -1.099051E-03 | 5.56 | 10.00 | 15.56 | 23.89 | 15.56 | 23.89
ElectricEIRChiller Trane RTHB 538kW/5.12COP/Valve EIRFT | 5.455087E-01 | -9.301201E-03 | 5.012361E-04 | 1.432870E-02 | 4.719381E-04 | -8.937669E-04 | 5.56 | 10.00 | 15.56 | 23.89 | 15.56 | 23.89
ElectricEIRChiller Trane RTHB 542kW/5.26COP/Valve EIRFT | 4.953775E-01 | -1.359340E-02 | 5.784637E-04 | 2.778142E-02 | 1.747259E-04 | -8.590768E-04 | 5.56 | 10.00 | 15.56 | 23.89 | 15.56 | 23.89
ElectricEIRChiller York YS 672kW/7.90COP/Valve EIRFT | 4.069331E-01 | -6.420922E-03 | 2.689257E-04 | 4.500373E-02 | 1.583981E-04 | -1.284532E-03 | 6.11 | 12.78 | 15.56 | 23.89 | 15.56 | 23.89
ElectricEIRChiller Carrier 23XL 686kW/5.91COP/Valve EIRFT | 5.014060E-01 | 1.561000E-03 | -1.347980E-04 | 1.525028E-02 | 5.701374E-04 | -1.221374E-03 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Trane RTHC 707kW/7.77COP/Valve EIRFT | 6.497944E-01 | 6.883157E-03 | -5.277681E-04 | 1.725788E-02 | 6.779317E-04 | -1.244055E-03 | 5.56 | 11.11 | 15.56 | 23.89 | 15.56 | 23.89
ElectricEIRChiller York YS 756kW/7.41COP/Valve EIRFT | 6.917947E-01 | -1.929936E-02 | 1.450011E-03 | 1.795987E-02 | 9.301685E-04 | -1.755165E-03 | 5.56 | 10.00 | 16.06 | 23.89 | 16.06 | 23.89
ElectricEIRChiller York YS 781kW/5.42COP/Valve EIRFT | 4.475957E-01 | -1.054652E-02 | 7.126870E-04 | 1.158632E-02 | 5.151510E-04 | -9.831355E-04 | 4.44 | 8.89 | 15.56 | 35.00 | 15.56 | 35.00
ElectricEIRChiller Carrier 23XL 830kW/6.97COP/Valve EIRFT | 4.610959E-01 | -1.560459E-02 | -2.737454E-04 | 2.650593E-02 | -7.789498E-05 | 1.855843E-04 | 5.56 | 10.00 | 14.17 | 23.89 | 14.17 | 23.89
ElectricEIRChiller Carrier 23XL 862kW/6.11COP/Valve EIRFT | 5.420642E-01 | -2.110032E-02 | 1.513908E-03 | 2.067897E-02 | 5.287518E-04 | -1.630330E-03 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 23XL 862kW/6.84COP/Valve EIRFT | 5.930611E-01 | -2.082914E-02 | 1.600282E-03 | 2.352564E-02 | 5.992247E-04 | -1.907335E-03 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller Carrier 23XL 865kW/6.05COP/Valve EIRFT | 5.437328E-01 | 7.625344E-03 | -9.201579E-05 | 1.339616E-03 | 8.286757E-04 | -1.543530E-03 | 3.33 | 7.78 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller York YS 879kW/5.82COP/Valve EIRFT | 5.595308E-01 | -1.087985E-02 | 8.721022E-04 | 1.010347E-02 | 5.087454E-04 | -1.211319E-03 | 3.33 | 7.78 | 12.78 | 29.44 | 12.78 | 29.44
ElectricEIRChiller Trane RTHC 1009kW/5.37COP/Valve EIRFT | 4.383883E-01 | 7.754235E-03 | 6.353809E-04 | -2.951880E-03 | 1.270756E-03 | -1.541831E-03 | 5.56 | 10.00 | 19.97 | 24.86 | 19.97 | 24.86
ElectricEIRChiller Trane RTHB 1051kW/5.05COP/Valve EIRFT | 4.904181E-01 | -5.530317E-03 | 1.209907E-03 | 9.122333E-03 | 5.923591E-04 | -1.469958E-03 | 4.44 | 8.89 | 23.89 | 35.00 | 23.89 | 35.00
ElectricEIRChiller Carrier 23XL 1062kW/5.50COP/Valve EIRFT | 2.634070E-01 | -7.025220E-03 | -4.942613E-04 | 2.516931E-02 | 1.712769E-04 | -4.309735E-04 | 6.67 | 10.00 | 21.11 | 29.44 | 21.11 | 29.44
ElectricEIRChiller Trane RTHC 1066kW/5.73COP/Valve EIRFT | 9.003080E-01 | 3.783201E-03 | 9.815780E-04 | -4.051727E-02 | 2.037095E-03 | -1.619326E-03 | 5.56 | 10.00 | 20.07 | 25.28 | 20.07 | 25.28
ElectricEIRChiller Trane RTHC 1094kW/6.55COP/Valve EIRFT | 6.579136E-01 | -1.133448E-02 | 6.497057E-04 | 7.318160E-03 | 6.167738E-04 | -9.553369E-04 | 5.56 | 10.00 | 15.56 | 23.89 | 15.56 | 23.89
ElectricEIRChiller Carrier 23XL 1108kW/6.92COP/Valve EIRFT | 5.668296E-01 | -2.800906E-02 | 9.362408E-04 | 2.210818E-02 | 4.660373E-04 | -7.989601E-04 | 5.56 | 10.00 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YS 1171kW/9.15COP/Valve EIRFT | 5.325834E-01 | -2.611733E-02 | 1.365012E-03 | 4.099324E-02 | 3.401995E-04 | -1.514251E-03 | 6.11 | 12.78 | 15.56 | 23.89 | 15.56 | 23.89
ElectricEIRChiller Carrier 23XL 1196kW/6.39COP/Valve EIRFT | 5.077824E-01 | -1.608447E-02 | 1.742121E-04 | 2.093857E-02 | 4.160938E-04 | -7.169668E-04 | 6.67 | 12.22 | 12.78 | 23.89 | 12.78 | 23.89
ElectricEIRChiller York YS 1554kW/9.31COP/Valve EIRFT | 5.099117E-01 | 1.379553E-02 | -2.069529E-04 | 2.846021E-02 | 7.189977E-04 | -2.027317E-03 | 5.56 | 8.89 | 15.56 | 35.00 | 15.56 | 35.00
ElectricEIRChiller York YS 1758kW/5.84COP/Valve EIRFT | 6.381264E-01 | 6.304193E-03 | 9.233511E-04 | -4.552881E-03 | 8.256904E-04 | -1.561533E-03 | 4.44 | 8.89 | 12.78 | 35.00 | 12.78 | 35.00
ElectricEIRChiller Trane CGWD 207kW/3.99COP/None EIRFT | 7.273870E-01 | -1.189276E-02 | 5.411677E-04 | 1.879294E-03 | 4.734664E-04 | -7.114850E-04 | 5.56 | 10.00 | 23.89 | 35.00 | 23.89 | 35.00

## CURVE QUADRATIC EIRFPLR
Name | Coeff1 Constant | Coeff2 x | Coeff3 x**2 | minimum value of x | maximum value of x
Curve名称 | 常熟项C1 | x的系数C2 | x2的系数C3 | x的最小值 | x的最大值
系数
ElectricEIRChiller McQuay WSC 471kW/5.89COP/Vanes EIRFPLR | 2.778889E-01 | 2.338363E-01 | 4.883748E-01 | 0.10 | 1.15
ElectricEIRChiller York YT 563kW/10.61COP/Vanes EIRFPLR | 5.203969E-01 | -7.775900E-01 | 1.255394E+00 | 0.09 | 1.03
ElectricEIRChiller McQuay PEH 703kW/7.03COP/Vanes EIRFPLR | 3.864389E-01 | -2.522595E-01 | 8.672354E-01 | 0.10 | 1.03
ElectricEIRChiller Carrier 23XL 724kW/6.04COP/Vanes EIRFPLR | 1.879418E-01 | 3.562862E-01 | 4.540392E-01 | 0.19 | 1.04
ElectricEIRChiller Carrier 19XR 742kW/5.42COP/VSD EIRFPLR | 1.202277E-01 | 1.396384E-01 | 7.394038E-01 | 0.19 | 1.02
ElectricEIRChiller McQuay WSC 816kW/6.74COP/Vanes EIRFPLR | 3.070136E-01 | 8.654874E-02 | 6.081551E-01 | 0.09 | 1.03
ElectricEIRChiller McQuay PEH 819kW/8.11COP/Vanes EIRFPLR | 2.830681E-01 | 2.254147E-01 | 4.916649E-01 | 0.09 | 1.05
ElectricEIRChiller Carrier 19XR 823kW/6.28COP/Vanes EIRFPLR | 2.965419E-01 | 4.689744E-01 | 2.332341E-01 | 0.10 | 1.03
ElectricEIRChiller Carrier 19XR 869kW/5.57COP/VSD EIRFPLR | 1.501042E-01 | -6.804336E-02 | 9.171460E-01 | 0.18 | 1.03
ElectricEIRChiller Carrier 19XR 897kW/7.23COP/VSD EIRFPLR | 2.036380E-01 | -3.913200E-01 | 1.187172E+00 | 0.20 | 1.04
ElectricEIRChiller Carrier 19XR 897kW/6.50COP/Vanes EIRFPLR | 3.323416E-01 | 2.561103E-01 | 4.106954E-01 | 0.20 | 1.02
ElectricEIRChiller York YT 897kW/7.60COP/VSD EIRFPLR | 4.708628E-02 | 7.070062E-02 | 8.802198E-01 | 0.10 | 1.02
ElectricEIRChiller York YT 897kW/6.27COP/VSD EIRFPLR | 9.836320E-02 | -1.638320E-02 | 9.127289E-01 | 0.10 | 1.02
ElectricEIRChiller Carrier 19XR 897kW/6.23COP/VSD EIRFPLR | 2.075556E-01 | -2.126466E-01 | 1.004182E+00 | 0.20 | 1.02
ElectricEIRChiller McQuay PFH 932kW/5.09COP/Vanes EIRFPLR | 6.823245E-02 | 6.672421E-01 | 2.654211E-01 | 0.09 | 1.02
ElectricEIRChiller York YT 960kW/4.64COP/Vanes EIRFPLR | 2.737941E-01 | 3.141127E-01 | 4.113671E-01 | 0.09 | 1.09
ElectricEIRChiller York YT 1023kW/5.81COP/Vanes EIRFPLR | 2.368399E-01 | 3.286421E-01 | 4.344939E-01 | 0.09 | 1.06
ElectricEIRChiller McQuay PEH 1030kW/8.58COP/Vanes EIRFPLR | 3.215320E-01 | -9.188416E-03 | 6.881582E-01 | 0.08 | 1.02
ElectricEIRChiller York YT 1048kW/6.06COP/Vanes EIRFPLR | 1.543796E-01 | 7.276121E-01 | 1.162393E-01 | 0.10 | 1.06
ElectricEIRChiller York YT 1055kW/5.96COP/Vanes EIRFPLR | 2.619878E-01 | 2.393605E-01 | 4.988306E-01 | 0.10 | 1.05
ElectricEIRChiller Carrier 19XR 1076kW/5.52COP/Vanes EIRFPLR | 1.315760E-01 | -3.004087E-02 | 8.967180E-01 | 0.10 | 1.02
ElectricEIRChiller Trane CVHE 1080kW/7.39COP/Vanes EIRFPLR | 1.789841E-01 | 2.976513E-01 | 5.243235E-01 | 0.20 | 1.05
ElectricEIRChiller York YT 1090kW/7.57COP/VSD EIRFPLR | 1.431969E-01 | -4.920686E-01 | 1.341333E+00 | 0.14 | 1.02
ElectricEIRChiller McQuay PEH 1104kW/8.00COP/Vanes EIRFPLR | 3.091150E-01 | -1.089639E-02 | 7.022967E-01 | 0.08 | 1.03
ElectricEIRChiller York YT 1125kW/7.92COP/VSD EIRFPLR | 1.147453E-01 | 4.231235E-02 | 8.419681E-01 | 0.09 | 1.03
ElectricEIRChiller Trane CVHE 1125kW/4.89COP/Vanes EIRFPLR | 1.807198E-01 | -1.469686E-01 | 9.658417E-01 | 0.10 | 1.01
ElectricEIRChiller York YT 1125kW/7.92COP/VSD EIRFPLR | 1.147453E-01 | 4.231235E-02 | 8.419681E-01 | 0.09 | 1.03
ElectricEIRChiller Trane CVHE 1129kW/7.19COP/Vanes EIRFPLR | 1.693841E-01 | 2.475201E-01 | 5.836059E-01 | 0.15 | 1.06
ElectricEIRChiller Carrier 19XR 1143kW/6.57COP/VSD EIRFPLR | 1.408822E-01 | -1.578153E-01 | 1.014316E+00 | 0.20 | 1.03
ElectricEIRChiller Carrier 19XR 1157kW/5.62COP/VSD EIRFPLR | 1.608589E-01 | -2.058215E-01 | 1.043133E+00 | 0.19 | 1.01
ElectricEIRChiller Carrier 19XR 1196kW/6.50COP/Vanes EIRFPLR | 2.724491E-01 | 2.710369E-01 | 4.552356E-01 | 0.20 | 1.03
ElectricEIRChiller Carrier 19XR 1213kW/7.78COP/Vanes EIRFPLR | 2.847744E-01 | 4.027863E-01 | 3.114896E-01 | 0.17 | 1.02
ElectricEIRChiller McQuay PEH 1231kW/6.18COP/Vanes EIRFPLR | 2.117054E-01 | 4.263662E-01 | 3.614654E-01 | 0.10 | 1.02
ElectricEIRChiller Carrier 19XR 1234kW/5.39COP/VSD EIRFPLR | 1.495681E-01 | -1.449639E-01 | 9.941070E-01 | 0.19 | 1.02
ElectricEIRChiller Carrier 19XR 1259kW/6.26COP/Vanes EIRFPLR | 2.226232E-01 | 5.199282E-01 | 2.578470E-01 | 0.18 | 1.03
ElectricEIRChiller York YK 1259kW/6.45COP/Vanes EIRFPLR | 1.014593E-01 | 6.216537E-01 | 2.780213E-01 | 0.18 | 1.02
ElectricEIRChiller York YT 1266kW/4.39COP/Vanes EIRFPLR | 7.326942E-01 | -7.962527E-01 | 1.059148E+00 | 0.11 | 1.05
ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes EIRFPLR | 2.324812E-01 | 7.690691E-01 | -6.532223E-04 | 0.20 | 1.02
ElectricEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes EIRFPLR | 2.324812E-01 | 7.690691E-01 | -6.532223E-04 | 0.20 | 1.02
ElectricEIRChiller Carrier 19XR 1294kW/7.61COP/Vanes EIRFPLR | 9.344563E-02 | 3.993002E-01 | 5.087169E-01 | 0.16 | 1.02
ElectricEIRChiller Trane CVHE 1329kW/5.38COP/Vanes EIRFPLR | 4.079777E-02 | 1.174456E+00 | -2.212711E-01 | 0.29 | 1.05
ElectricEIRChiller Carrier 19XR 1350kW/7.90COP/VSD EIRFPLR | 3.336374E-01 | -4.098166E-01 | 1.077791E+00 | 0.19 | 1.02
ElectricEIRChiller York YT 1368kW/7.35COP/VSD EIRFPLR | 9.483562E-02 | 1.521114E-01 | 7.543027E-01 | 0.10 | 1.03
ElectricEIRChiller Trane CVHE 1372kW/7.49COP/Vanes EIRFPLR | 5.154478E-02 | 9.635713E-01 | -1.896824E-02 | 0.41 | 1.07
ElectricEIRChiller York YT 1396kW/7.35COP/Vanes EIRFPLR | 3.043032E-01 | 3.720107E-02 | 6.590338E-01 | 0.10 | 1.03
ElectricEIRChiller Carrier 19XR 1403kW/7.09COP/VSD EIRFPLR | 8.788698E-02 | 2.678891E-01 | 6.445180E-01 | 0.17 | 1.03
ElectricEIRChiller York YT 1403kW/6.94COP/VSD EIRFPLR | 3.272242E-02 | 3.873540E-01 | 5.789579E-01 | 0.10 | 1.1
ElectricEIRChiller Trane CVHE 1407kW/7.14COP/VSD EIRFPLR | 5.963988E-02 | 3.503067E-01 | 5.870000E-01 | 0.30 | 1.06
ElectricEIRChiller McQuay PFH 1407kW/6.60COP/Vanes EIRFPLR | 7.700603E-02 | 5.414789E-01 | 3.826334E-01 | 0.10 | 1.04
ElectricEIRChiller Carrier 19XR 1407kW/6.04COP/VSD EIRFPLR | 1.188880E-01 | 6.723542E-01 | 2.068754E-01 | 0.20 | 1.04
ElectricEIRChiller Carrier 19XR 1410kW/8.54COP/VSD EIRFPLR | 9.662908E-02 | 7.475978E-01 | 1.566368E-01 | 0.18 | 1.03
ElectricEIRChiller Trane CVHE 1442kW/6.61COP/VSD EIRFPLR | 9.299787E-02 | 3.244475E-01 | 5.818753E-01 | 0.10 | 1.07
ElectricEIRChiller York YT 1459kW/6.40COP/VSD EIRFPLR | 3.999642E-02 | 2.509430E-01 | 7.067059E-01 | 0.10 | 1.13
ElectricEIRChiller Trane CVHE 1484kW/9.96COP/VSD EIRFPLR | 1.353827E-01 | 1.385983E-02 | 8.522688E-01 | 0.24 | 1.06
ElectricEIRChiller York YT 1495kW/7.51COP/VSD EIRFPLR | 1.517470E-01 | -1.577252E-01 | 1.005197E+00 | 0.11 | 1.05
ElectricEIRChiller McQuay WSC 1519kW/7.10COP/Vanes EIRFPLR | 1.563837E-01 | 4.894381E-01 | 3.541551E-01 | 0.10 | 1.03
ElectricEIRChiller Carrier 19XR 1558kW/5.81COP/VSD EIRFPLR | 1.620909E-01 | -2.553890E-01 | 1.092232E+00 | 0.19 | 1.01
ElectricEIRChiller Carrier 19XR 1586kW/5.53COP/VSD EIRFPLR | 1.996379E-01 | -1.612021E-01 | 9.608483E-01 | 0.19 | 1.01
ElectricEIRChiller McQuay PEH 1635kW/7.47COP/Vanes EIRFPLR | 1.836695E-01 | 5.781685E-01 | 2.385719E-01 | 0.08 | 1.03
ElectricEIRChiller Carrier 19XR 1635kW/6.36COP/Vanes EIRFPLR | 2.581595E-01 | 2.707154E-01 | 4.707425E-01 | 0.18 | 1.05
ElectricEIRChiller Carrier 19XR 1656kW/8.24COP/VSD EIRFPLR | 1.982584E-01 | 4.414042E-02 | 7.642946E-01 | 0.17 | 1.04
ElectricEIRChiller York YT 1663kW/9.34COP/Vanes EIRFPLR | 2.127966E-01 | 3.131004E-01 | 4.726018E-01 | 0.17 | 1.03
ElectricEIRChiller Carrier 19XL 1674kW/7.89COP/Vanes EIRFPLR | 3.386410E-01 | 2.621224E-01 | 3.987109E-01 | 0.32 | 1.02
ElectricEIRChiller Trane CVHF 1681kW/6.59COP/Vanes EIRFPLR | 1.619116E-01 | 2.362420E-01 | 6.032459E-01 | 0.10 | 1.02
ElectricEIRChiller Carrier 19XR 1723kW/8.32COP/VSD EIRFPLR | 2.374010E-01 | -1.796745E-01 | 9.441507E-01 | 0.18 | 1.04
ElectricEIRChiller Carrier 19XR 1727kW/9.04COP/Vanes EIRFPLR | 2.465824E-01 | 4.494453E-01 | 3.037680E-01 | 0.17 | 1.03
ElectricEIRChiller McQuay WSC 1751kW/6.73COP/Vanes EIRFPLR | 2.250725E-01 | 2.648297E-01 | 5.095786E-01 | 0.10 | 1.06
ElectricEIRChiller Trane CVHF 1758kW/5.96COP/Vanes EIRFPLR | 3.694797E-01 | 9.551656E-02 | 5.347291E-01 | 0.20 | 1.02
ElectricEIRChiller York YT 1758kW/5.76COP/VSD EIRFPLR | 7.859908E-02 | 1.950291E-01 | 7.241581E-01 | 0.10 | 1.02
ElectricEIRChiller York YT 1758kW/6.26COP/Vanes EIRFPLR | 1.720545E-01 | 5.598164E-01 | 2.626117E-01 | 0.10 | 1.14
ElectricEIRChiller York YT 1758kW/5.96COP/Vanes EIRFPLR | 2.236154E-01 | 2.590053E-01 | 5.169137E-01 | 0.10 | 1.01
ElectricEIRChiller Trane CVHE 1758kW/5.96COP/Vanes EIRFPLR | 1.871377E-01 | 5.849639E-01 | 2.291447E-01 | 0.20 | 1.03
ElectricEIRChiller York YT 1758kW/6.28COP/Vanes EIRFPLR | 1.861223E-01 | 5.482049E-01 | 2.647377E-01 | 0.20 | 1.06
ElectricEIRChiller Carrier 19XR 1758kW/5.86COP/VSD EIRFPLR | 2.784580E-01 | -5.498632E-01 | 1.269693E+00 | 0.20 | 1.02
ElectricEIRChiller Trane CVHF 1758kW/6.46COP/VSD EIRFPLR | 3.268954E-01 | 3.297771E-01 | 3.423342E-01 | 0.20 | 1.02
ElectricEIRChiller Trane CVHF 1758kW/6.87COP/Vanes EIRFPLR | 2.401900E-01 | 5.090345E-01 | 2.500532E-01 | 0.20 | 1.03
ElectricEIRChiller Carrier 19XR 1776kW/8.00COP/Vanes EIRFPLR | 3.276235E-01 | 2.787167E-01 | 3.952405E-01 | 0.17 | 1.04
ElectricEIRChiller Carrier 19XL 1779kW/6.18COP/Vanes EIRFPLR | 3.090532E-01 | 2.641442E-01 | 4.269265E-01 | 0.20 | 1.03
ElectricEIRChiller Trane CVHF 1779kW/6.18COP/Vanes EIRFPLR | 1.699409E-01 | 1.874304E-01 | 6.410385E-01 | 0.10 | 1.02
ElectricEIRChiller York YT 1794kW/8.11COP/Vanes EIRFPLR | 3.187543E-02 | 8.272483E-01 | 1.279099E-01 | 0.10 | 1.08
ElectricEIRChiller York YT 1794kW/7.90COP/VSD EIRFPLR | 1.445880E-01 | 1.059293E-01 | 7.489704E-01 | 0.10 | 1.05
ElectricEIRChiller Carrier 19XL 1797kW/5.69COP/Vanes EIRFPLR | 5.926251E-01 | -2.657314E-01 | 6.731751E-01 | 0.39 | 1.01
ElectricEIRChiller Carrier 19XR 1801kW/6.34COP/VSD EIRFPLR | 1.040764E-01 | 2.818752E-01 | 6.144036E-01 | 0.20 | 1.03
ElectricEIRChiller York YT 1867kW/10.09COP/Vanes EIRFPLR | 2.157002E-01 | 2.251016E-01 | 5.584287E-01 | 0.09 | 1.04
ElectricEIRChiller Carrier 19XL 1871kW/6.49COP/Vanes EIRFPLR | 2.984908E-01 | 2.906868E-01 | 4.089411E-01 | 0.19 | 1.02
ElectricEIRChiller York YT 1881kW/6.77COP/VSD EIRFPLR | 6.087656E-02 | 4.842164E-01 | 4.571519E-01 | 0.09 | 1.03
ElectricEIRChiller York YK 1881kW/6.53COP/Vanes EIRFPLR | 3.626231E-02 | 5.378739E-01 | 4.265341E-01 | 0.19 | 1.03
ElectricEIRChiller York YK 1881kW/6.53COP/Vanes EIRFPLR | 5.272116E-02 | 4.176382E-01 | 5.310870E-01 | 0.19 | 1.03
ElectricEIRChiller McQuay PEH 1895kW/6.42COP/Vanes EIRFPLR | 2.592598E-01 | 1.425462E-01 | 5.966041E-01 | 0.09 | 1.09
ElectricEIRChiller York YT 1934kW/7.55COP/Vanes EIRFPLR | 1.706237E-01 | 6.063362E-01 | 2.170672E-01 | 0.10 | 1.06
ElectricEIRChiller McQuay PEH 1934kW/6.01COP/Vanes EIRFPLR | 3.849256E-01 | -2.369152E-01 | 8.496351E-01 | 0.10 | 1.08
ElectricEIRChiller McQuay WDC 1973kW/6.28COP/Vanes EIRFPLR | 1.282891E-01 | 2.722981E-01 | 6.012232E-01 | 0.09 | 1.06
ElectricEIRChiller York YK 1997kW/7.24COP/Vanes EIRFPLR | 9.359332E-02 | 5.873752E-01 | 3.208990E-01 | 0.18 | 1.06
ElectricEIRChiller McQuay PFH 2043kW/8.44COP/Vanes EIRFPLR | 1.225600E-01 | 3.070007E-01 | 5.712759E-01 | 0.08 | 1.02
ElectricEIRChiller Trane CVHF 2043kW/9.08COP/Vanes EIRFPLR | 2.173752E-01 | 4.394720E-01 | 3.431813E-01 | 0.28 | 1.04
ElectricEIRChiller Carrier 19XL 2057kW/6.05COP/Vanes EIRFPLR | 4.041274E-01 | -3.861525E-01 | 9.804493E-01 | 0.28 | 1.04
ElectricEIRChiller York YT 2110kW/7.15COP/Vanes EIRFPLR | 2.469187E-01 | 1.862690E-01 | 5.660904E-01 | 0.10 | 1.04
ElectricEIRChiller McQuay PFH 2124kW/6.03COP/Vanes EIRFPLR | 1.051419E-01 | 2.033679E-01 | 6.902026E-01 | 0.09 | 1.03
ElectricEIRChiller York YK 2159kW/6.85COP/Vanes EIRFPLR | 2.595694E-01 | 1.889684E-01 | 5.518450E-01 | 0.14 | 1.05
ElectricEIRChiller Trane CVHF 2184kW/6.78COP/Vanes EIRFPLR | 8.942647E-02 | 5.249540E-01 | 3.850801E-01 | 0.09 | 1.01
ElectricEIRChiller York YK 2201kW/6.69COP/Vanes EIRFPLR | 2.653493E-01 | 1.444620E-01 | 5.911158E-01 | 0.14 | 1.05
ElectricEIRChiller York YT 2233kW/9.54COP/VSD EIRFPLR | 7.308728E-02 | 1.513521E-01 | 7.709311E-01 | 0.10 | 1.04
ElectricEIRChiller York YT 2233kW/9.54COP/VSD EIRFPLR | 6.917141E-02 | 1.743339E-01 | 7.524059E-01 | 0.10 | 1.04
ElectricEIRChiller York YK 2237kW/6.41COP/Vanes EIRFPLR | 2.605354E-01 | 2.125571E-01 | 5.269144E-01 | 0.13 | 1.01
ElectricEIRChiller York YK 2275kW/6.32COP/Vanes EIRFPLR | 2.702822E-01 | 1.837680E-01 | 5.455683E-01 | 0.13 | 1.02
ElectricEIRChiller York YK 2275kW/6.32COP/Vanes EIRFPLR | 2.735485E-01 | 2.163041E-01 | 5.099054E-01 | 0.13 | 1.03
ElectricEIRChiller Trane CVHF 2300kW/8.10COP/Vanes EIRFPLR | 1.161399E-01 | 4.347344E-01 | 4.486380E-01 | 0.23 | 1.02
ElectricEIRChiller Trane CVHF 2317kW/6.33COP/VSD EIRFPLR | 9.861441E-02 | 5.297727E-01 | 3.707229E-01 | 0.10 | 1.04
ElectricEIRChiller Carrier 19XR 2391kW/6.77COP/Vanes EIRFPLR | 3.036386E-01 | 2.524850E-01 | 4.429285E-01 | 0.20 | 1.02
ElectricEIRChiller Carrier 19XR 2391kW/6.44COP/VSD EIRFPLR | 9.774812E-02 | 2.490111E-01 | 6.539378E-01 | 0.20 | 1.02
ElectricEIRChiller York YK 2412kW/5.58COP/Vanes EIRFPLR | 2.472427E-01 | 7.531481E-01 | 8.643617E-04 | 0.12 | 1.01
ElectricEIRChiller McQuay PFH 2462kW/6.67COP/Vanes EIRFPLR | 9.222135E-02 | 5.830980E-01 | 3.250019E-01 | 0.10 | 1.02
ElectricEIRChiller Trane CVHF 2567kW/11.77COP/VSD EIRFPLR | 1.039419E-01 | 4.184975E-01 | 4.774210E-01 | 0.11 | 1.04
ElectricEIRChiller York YK 2771kW/6.84COP/VSD EIRFPLR | 8.653354E-02 | 1.737382E-01 | 7.403679E-01 | 0.20 | 1.02
ElectricEIRChiller Trane CVHF 2799kW/6.40COP/Vanes EIRFPLR | 3.023576E-01 | -2.893592E-02 | 7.262269E-01 | 0.20 | 1.04
ElectricEIRChiller York YT 3133kW/9.16COP/Vanes EIRFPLR | 1.387579E-01 | 6.435208E-01 | 2.155990E-01 | 0.07 | 1.03
ElectricEIRChiller McQuay PFH 3165kW/6.48COP/Vanes EIRFPLR | 1.054110E-01 | 4.090646E-01 | 4.838839E-01 | 0.10 | 1.03
ElectricEIRChiller McQuay PFH 4020kW/7.35COP/Vanes EIRFPLR | 5.763566E-02 | 5.964012E-01 | 3.473613E-01 | 0.14 | 1.03
ElectricEIRChiller York YK 4396kW/6.63COP/Vanes EIRFPLR | 3.021070E-01 | 3.103971E-02 | 6.669726E-01 | 0.41 | 1.06
ElectricEIRChiller York YK 4477kW/6.64COP/Vanes EIRFPLR | 2.767206E-01 | 1.074393E-01 | 6.145706E-01 | 0.41 | 1.06
ElectricEIRChiller York YK 4515kW/6.22COP/Vanes EIRFPLR | 2.870815E-01 | 3.951784E-01 | 3.177735E-01 | 0.40 | 1.03
ElectricEIRChiller York YK 4537kW/6.28COP/Vanes EIRFPLR | 2.528426E-01 | 2.920280E-01 | 4.533447E-01 | 0.40 | 1.03
ElectricEIRChiller Trane CVHF 4610kW/6.34COP/Vanes EIRFPLR | 2.026691E-01 | 2.922585E-01 | 5.044422E-01 | 0.20 | 1.02
ElectricEIRChiller Carrier 19EX 4667kW/6.16COP/Vanes EIRFPLR | 3.771252E-01 | 2.854188E-02 | 5.928670E-01 | 0.40 | 1.04
ElectricEIRChiller Trane CVHF 4677kW/6.27COP/Vanes EIRFPLR | 3.531562E-01 | -2.126229E-01 | 8.597400E-01 | 0.41 | 1.03
ElectricEIRChiller York YK 4966kW/6.05COP/Vanes EIRFPLR | 3.416463E-01 | 1.947185E-01 | 4.640804E-01 | 0.12 | 1.02
ElectricEIRChiller York YK 4969kW/7.14COP/Vanes EIRFPLR | 2.259512E-01 | 2.320151E-01 | 5.423771E-01 | 0.16 | 1.07
ElectricEIRChiller York YK 4969kW/7.07COP/Vanes EIRFPLR | 2.308102E-01 | 1.802734E-01 | 5.894894E-01 | 0.16 | 1.06
ElectricEIRChiller Carrier 19EX 4997kW/6.40COP/Vanes EIRFPLR | 3.364887E-01 | 2.122607E-01 | 4.486522E-01 | 0.40 | 1.05
ElectricEIRChiller Carrier 19EX 5148kW/6.34COP/Vanes EIRFPLR | 1.883602E-01 | 5.018646E-01 | 3.089569E-01 | 0.20 | 1.03
ElectricEIRChiller York YK 5170kW/7.15COP/Vanes EIRFPLR | 2.497273E-01 | 1.011288E-01 | 6.499847E-01 | 0.15 | 1.08
ElectricEIRChiller Carrier 19EX 5208kW/6.88COP/Vanes EIRFPLR | 2.334262E-01 | 3.926783E-01 | 3.731320E-01 | 0.20 | 1.03
ElectricEIRChiller York YK 5465kW/6.94COP/Vanes EIRFPLR | 2.795792E-01 | 7.872758E-02 | 6.424321E-01 | 0.14 | 1.07
ElectricEIRChiller York YK 5549kW/6.50COP/Vanes EIRFPLR | 2.336623E-01 | 1.901320E-01 | 5.749473E-01 | 0.14 | 1.05
ElectricEIRChiller Carrier 19FA 5651kW/5.50COP/Vanes EIRFPLR | 1.629327E-01 | 5.709336E-01 | 2.659304E-01 | 0.19 | 1.02
DOE-2 Centrifugal/5.50COP EIRFPLR | 0.222903 | 0.313387 | 0.463710 | 0.0 | 1.0
ElectricEIRChiller Multistack MS 172kW/3.67COP/None EIRFPLR | 4.747786E-03 | 1.072374E+00 | -7.758317E-02 | 0.40 | 1.03
DOE-2 Reciprocating/3.67COP EIRFPLR | 0.088065 | 1.137742 | -0.225806 | 0.0 | 1.0
ElectricEIRChiller Trane RTWA 383kW/4.17COP/Valve EIRFPLR | 3.295553E-02 | 9.114398E-01 | 5.565265E-02 | 0.25 | 1.01
ElectricEIRChiller Trane RTHB 531kW/4.83COP/Valve EIRFPLR | 1.980020E-01 | 2.733157E-01 | 5.277318E-01 | 0.30 | 1.01
ElectricEIRChiller Trane RTHB 538kW/5.12COP/Valve EIRFPLR | 1.816950E-01 | 3.731838E-01 | 4.448009E-01 | 0.30 | 1.01
ElectricEIRChiller Trane RTHB 542kW/5.26COP/Valve EIRFPLR | 3.057645E-01 | -1.548084E-01 | 8.484536E-01 | 0.30 | 1.01
ElectricEIRChiller York YS 672kW/7.90COP/Valve EIRFPLR | 1.936152E-01 | 3.375574E-01 | 4.704892E-01 | 0.09 | 1.01
ElectricEIRChiller Carrier 23XL 686kW/5.91COP/Valve EIRFPLR | 2.113934E-01 | 4.190226E-01 | 3.686143E-01 | 0.20 | 1.04
ElectricEIRChiller Trane RTHC 707kW/7.77COP/Valve EIRFPLR | 1.997099E-01 | 6.754676E-01 | 1.243767E-01 | 0.28 | 1.01
ElectricEIRChiller York YS 756kW/7.41COP/Valve EIRFPLR | 2.929778E-01 | 1.673799E-02 | 6.881229E-01 | 0.11 | 1.01
ElectricEIRChiller York YS 781kW/5.42COP/Valve EIRFPLR | 2.519108E-01 | 2.756914E-01 | 4.725826E-01 | 0.09 | 1.01
ElectricEIRChiller Carrier 23XL 830kW/6.97COP/Valve EIRFPLR | 2.307464E-01 | 7.784162E-01 | -7.516503E-03 | 0.20 | 1.01
ElectricEIRChiller Carrier 23XL 862kW/6.11COP/Valve EIRFPLR | 2.292819E-01 | 3.662723E-01 | 4.032019E-01 | 0.20 | 1.04
ElectricEIRChiller Carrier 23XL 862kW/6.84COP/Valve EIRFPLR | 1.145826E-01 | 7.340475E-01 | 1.507744E-01 | 0.30 | 1.04
ElectricEIRChiller Carrier 23XL 865kW/6.05COP/Valve EIRFPLR | 2.545235E-01 | 3.104981E-01 | 4.347781E-01 | 0.20 | 1.03
ElectricEIRChiller York YS 879kW/5.82COP/Valve EIRFPLR | 3.029493E-01 | 3.223124E-01 | 3.751948E-01 | 0.10 | 1.02
ElectricEIRChiller Trane RTHC 1009kW/5.37COP/Valve EIRFPLR | 1.316727E-01 | 1.013111E+00 | -1.413213E-01 | 0.30 | 1.01
ElectricEIRChiller Trane RTHB 1051kW/5.05COP/Valve EIRFPLR | 2.590465E-01 | 2.148987E-01 | 5.265039E-01 | 0.20 | 1.01
ElectricEIRChiller Carrier 23XL 1062kW/5.50COP/Valve EIRFPLR | 2.576261E-01 | 3.416910E-01 | 4.007672E-01 | 0.20 | 1.01
ElectricEIRChiller Trane RTHC 1066kW/5.73COP/Valve EIRFPLR | 1.007344E-01 | 1.119205E+00 | -2.173230E-01 | 0.30 | 1.01
ElectricEIRChiller Trane RTHC 1094kW/6.55COP/Valve EIRFPLR | 1.626466E-01 | 7.903550E-01 | 4.770888E-02 | 0.25 | 1.01
ElectricEIRChiller Carrier 23XL 1108kW/6.92COP/Valve EIRFPLR | 1.370745E-01 | 8.374817E-01 | 2.534280E-02 | 0.20 | 1.02
ElectricEIRChiller York YS 1171kW/9.15COP/Valve EIRFPLR | 1.889392E-01 | 4.684305E-01 | 3.451545E-01 | 0.09 | 1.01
ElectricEIRChiller Carrier 23XL 1196kW/6.39COP/Valve EIRFPLR | 1.061065E-01 | 7.305514E-01 | 1.632883E-01 | 0.20 | 1.03
ElectricEIRChiller York YS 1554kW/9.31COP/Valve EIRFPLR | 1.720219E-01 | 5.084848E-01 | 3.212462E-01 | 0.10 | 1.02
ElectricEIRChiller York YS 1758kW/5.84COP/Valve EIRFPLR | 3.149879E-01 | 3.171267E-01 | 3.709077E-01 | 0.20 | 1.04
ElectricEIRChiller Trane CGWD 207kW/3.99COP/None EIRFPLR | 4.146742E-02 | 6.543795E-01 | 3.044125E-01 | 0.25 | 1.01